## DMREZ
| 92-15-7 {04/2003}--27c | [17 empty] | Page 1 of 4 | [7 empty] | Bowery Bay | [5 empty] | Page 2 of 4 |  | Bowery Bay | [15 empty] | Page 3 of 4 |  |  | 2016-03-01 | 2016 |  |  | Bowery Bay | [6 empty] | Page 4 of 4
| NEW YORK STATE DEPARTMENT OF ENVIRONMENTAL CONSERVATION | [140 empty] | Minimum Effluent pH
| DIVISION OF WATER | [70 empty] | Loadings Calculations Are Done Here {Total Flow TSS & CBOD Loadings are now reported on DMR and tabs} | [13 empty] | NITROGEN CALCULATIONS DONE HERE | [14 empty] | 7-DAY ARITMETIC MEAN CALCULATIONS | [27 empty] | DAILY FLOW - 12-MONTH ROLLING AVERAGE CALCULATION | [12 empty] | Violation Counting
| WASTEWATER FACILITY OPERATION REPORT FOR THE MONTH OF: | [5 empty] | 2016-03-01 | 2016 | [13 empty] | 2016-03-01 | 2016 | [12 empty] | 2016-03-01 | 2016 | [14 empty] | Effects on Receiving Stream |  |  |  |  | Name and amount of chemicals used in treatment |  |  |  |  | Plant Sludge Production (digested sludge to storage): | [9 empty] | If a number is starred, it is replaced by the arithmetic mean for all calculations. | [13 empty] | (For ALL Plants)
| SPDES PERMIT No. |  |  | FACILITY NAME |  |  | FACILITY OWNER | [8 empty] | FACILITY LOCATION |  |  |  |  | FACILITY MAILING ADDRESS [Street, City, State, Zip code] | [5 empty] | TELEPHONE NUMBER |  |  |  |  | CHIEF OPERATOR'S NAME | Certification Grade | [13 empty] | ACTIVATED SLUDGE |  |  |  |  | Rikers Island Channel |  |  |  |  | process during month: |  |  |  |  | a. | Amount | 2037500 | cubic feet | If needed, don't forget to multiply by 1000 | [15 empty] | For use in Percent Removal Calculations | [18 empty] | NUMBER OF DAYS IN CURRENT MONTH |  |  | 31
| NY-0026158 |  |  | Bowery Bay |  |  | New York City Department of Environmental Protection | [8 empty] | 4301 Berrian Blvd., Astoria, New York 12115 |  |  |  |  | 4301 Berrian Blvd., Astoria, New York 11211 | [5 empty] | (718) 595-5050 |  |  |  |  | Mr. Eric Klee | Grade 4A | [13 empty] | PROCESS CONTROL | [9 empty] | a. | Sodium Hypochlorite | 85062 | gallons |  | b. | Solid Content | 1.9 | % | [5 empty] | parameter | column |  | Daily Loadings based on Dry Flow |  |  |  | Daily Loadings based on Daily Flow |  |  |  | {starred values replaced with monthly avg conc} |  |  |  | {starred values replaced with monthly average concentrations}
|  |  | Volume of Sewage Treated |  |  |  | Temperature (C) | pH (S.U.) | [5 empty] | Settleable Solids (ml/L) |  | CBOD5 (mg/L) |  | Total Suspended Solids (mg/L) |  |  |  |  | Total Phosphorous (mg/L) |  | Orthophosphate (mg/L) |  | Chlorine Residual | Fecal Coliform |  | Enterococcus |  | REMARKS |  |  |  | Nitrogen Series (mg/L) | [7 empty] | DO | Chlorides | Sample | Average | Aerator | Settleable Sludge | Return | Waste | DATE | STATION | PARAMETER | RESULT |  | b. | Caustic Soda | 0 | gallons |  | c. | Volatile Solids Content | 69.1 | % | [5 empty] | dry flow | e | Ar. Means | 144 | 6 | 149 | 12 |  |  |  |  | {Wet flow concentrations removed} |  |  |  | 0.07 | 0.1 | 28.5 | 37.7 | 1.19 | 2.55 | 8.7 | 9.9 | [23 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 |  |  | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103
|  |  | Dry Flow | Inst. Max. | Daily Average | Inst. Min | Effluent | Influent | Influent | Influent | Effluent | Effluent | Effluent | Influent | Effluent | Influent | Effluent | Influent | Effluent | Violation of |  |  | Influent | Effluent | Influent | Effluent | Effluent (mg/L) | Effluent |  | Effluent |  | Enter any other comments, observations, operating |  |  |  | Influent |  |  |  | Effluent |  |  |  | Effluent | Influent | Type | Aerator | Effluent | Volume mg/L | Act. Sludge | Act. Sludge | [5 empty] | c. | Ferric Chloride | 0 | gallons |  | d. | Dewatered At: | WI & HP | [6 empty] | daily flow | g |  | Inf. CBOD | Eff. CBOD | Inf. TSS | Eff. TSS | Inf. CBOD | Eff. CBOD | Inf. TSS | Eff. TSS | Inf. CBOD | Eff. CBOD | Inf. TSS | Eff. TSS | Influent (mg/L) |  |  |  | Effluent (mg/L) |  |  |  | Total Nitrogen | Total Nitrogen | TN w/ Total Flow | TN w/ Total Flow | TKN w/ Total Flow | TKN w/ Total Flow | [17 empty] | 7-DAY ARITHMETIC MEAN CALCULATIONS | [9 empty] | [GEOMEAN] |  | *** MANUALLY UPDATE *** | [13 empty] | Effluent
| Day | Date | MGD | MGD | MGD | MGD | (2) | Minimum | Maximum | Average | Minimum | Maximum | Average | Average | Average | 24-hour comp | 24-hour comp | 24-hour comp | 24-hour comp | daily TSS limit? | DAY | DATE | 24-hour comp | 24-hour comp | 24-hour comp | 24-hour comp | Daily Average | MF FC/100ml |  | MF E/100ml |  | problems, equipment failure, etc. | Logged Weather | DAY | DATE | NO2 (as N) | NO3 (as N) | NH3 (as NH3) | TKN (as N) | NO2 (as N) | NO3 (as N) | NH3 (as NH3) | TKN (as N) | mg/L | mg/L |  | SS mg/L | SS mg/L | (SSV) 30 Minutes | RAS (MGD) | WAS lbs/day | [5 empty] | d. | Polymer Cationic | 1020 | gallons |  | Dewatering: |  |  |  | If you have dewatering, move this over to cell BL10 |  |  |  |  | inf cbod | r | Day | Dry #/d | Dry #/d | Dry #/d | Dry #/d | Total #/d | Total #/d | Total #/d | Total #/d | mg/L | mg/L | mg/L | mg/L | NO2 | NO3 | NH3 | TKN | NO2 | NO3 | NH3 | TKN | Influent (mg/L) | Effluent (mg/L) | Influent (lbs/day) | Effluent (lbs/day) | Influent (lbs/day) | Effluent (lbs/day) |  |  | 7 | Flows (MGD) |  | A R I T H M E T I C M E A N S - Concentrations |  |  |  | GEO MEAN | A R I T H M E T I C M E A N S - LOADS (Daily Flow) |  |  |  |  | DAY | DATE | Dry Flow Avg | Total Flow Avg | TSS Inf Conc | TSS Inf Load | TSS Eff Conc | TSS Eff Load | CBOD Inf Conc | CBOD Inf Load | CBOD Eff Conc | CBOD Eff Load | Fecal Coliform |  | MONTH | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 |  | Minimum
update D11 only, F9 | 2016-03-01 | 2016-03-01 | 86 | 156 | 94 | 60 | 17 | 6.7 | 7 | 6.9 | 6.4 | 7.4 | 6.7 |  |  | 146 | 5 | 119 | 7 |  | 2016-03-01 | 2016-03-01 | 4.5445 | 1.49 | 2.635 | 1.27 | 0.44 |  | 128 |  |  |  | Rain | 2016-03-01 | 2016-03-01 | 0.04 | 0.146 | 27.609 | 37.4 | 0.83 | 2.8 | 11.8 | 12.1 | 4.1 | 120 |  | 4760 | 4320 | 290 | 50 | 127103 | [5 empty] | e. | Polymer Anionic | 0 | gallons |  | a. | Amount of Cake | 0 | wet tons | Dewatering: |  |  |  |  | eff cbod | s | 2016-03-01 | 104717.04 | 3586.2 | 85351.56 | 5020.68 | 114458.16 | 3919.8 | 93291.24 | 5487.72 | 146 | 5 | 119 | 7 | 0.04 | 0.146 | 27.609 | 37.4 | 0.83 | 2.8 | 11.8 | 12.1 | 37.6 | 15.7 | 29476.896 | 12308.172 | 29320.104 | 9485.916 | 2016-03-01 | Week Dates (Sun-Sat) |  | Dry Flow | Total Flow | TSS Inf Conc | TSS Eff Conc | CBOD Inf Conc | CBOD Eff Conc | Fecal Coliform | TSS Inf Load | TSS Eff Load | CBOD Inf Load | CBOD Eff Load | 3 | 2016-03-01 | 2016-03-01 | [12 empty] | FLOW | 103 | 112 | 91 | 103 | 98 | 116 | 103 | 100 | 101 | 105 | 98 | 105 |  | 0
i.e., 04/01/08 | 2016-03-02 | 2016-03-02 | 85 | 171 | 98 | 47 | 17 | 6.6 | 7.2 | 6.9 | 6.4 | 6.6 | 6.5 |  |  | 138 | 21 | 128 | 72 | violation | 2016-03-02 | 2016-03-02 |  |  |  |  | 0.43 |  | 92 |  |  | Daily Effluent TSS Concentration > 50 mg/L | Rain | 2016-03-02 | 2016-03-02 | 0.1165 | 0.24 | 22.154 | 31.455 | 0.86 | 2.73 | 11.3 | 16.2 | 3.76 |  |  | 3620 | 2100 | 210 | 55 | 140102 | [10 empty] | b. | Solid Content |  | % | a. | Amount of Cake |  | wet tons |  | inf tss | t | 2016-03-02 | 97828.2 | 14886.9 | 90739.2 | 51040.8 | 112790.16 | 17163.72 | 104616.96 | 58847.04 | 138 | 21 | 128 | 72 | 0.1165 | 0.24 | 22.154 | 31.455 | 0.86 | 2.73 | 11.3 | 16.2 | 31.8 | 19.8 | 25990.776 | 16182.936 | 25708.8006 | 13240.584 | 2016-03-02 | 2016-02-28 | 2016-03-05 | 87 | 91 | 130 | 20 | 151 | 8 | 91 | 99100 | 15600 | 114200 | 6100 | 4 | 2016-03-02 | 2016-03-02 | [12 empty] | Do NOT "move" the months - just update the year and the flow for the current month. | [13 empty] | 0
| 2016-03-03 | 2016-03-03 | 82 | 97 | 82 | 48 | 17 | 6.6 | 7.4 | 6.9 | 6.3 | 6.5 | 6.4 |  |  | 178 | 8 | 133 | 20 |  | 2016-03-03 | 2016-03-03 |  |  |  |  | 0.6 |  | 109 |  |  |  | Clear | 2016-03-03 | 2016-03-03 | 0.123 | 0.126 | 28.69 | 38.56 | 1.06 | 3.09 | 10.8 | 11.7 | 4.64 |  |  | 4620 | 2860 | 330 | 59 | 98167 | [5 empty] | Amount of electrical power consumed |  |  |  |  | c. | Volatile Solids Content |  | % | b. | Solid Content |  | % |  | eff tss | u | 2016-03-03 | 121730.64 | 5471.04 | 90956.04 | 13677.6 | 121730.64 | 5471.04 | 90956.04 | 13677.6 | 178 | 8 | 133 | 20 | 0.123 | 0.126 | 28.69 | 38.56 | 1.06 | 3.09 | 10.8 | 11.7 | 38.8 | 15.9 | 26534.544 | 10873.692 | 26370.4128 | 8001.396 | 2016-03-03 | 2016-03-06 | 2016-03-12 | 88 | 88 | 155 | 9 | 143 | 6 | 90 | 113700 | 6500 | 105000 | 4200 | 5 | 2016-03-03 | 2016-03-03 | [12 empty] | e.g. for April 2003 - replace "ARP 02" with "APR 03" in cell EK10, and manually enter the flow from cell EK17 into cell EK11 | [13 empty] | 0
| 2016-03-04 | 2016-03-04 | 90 | 146 | 96 | 43 | 17 | 6.6 | 7.3 | 7 | 6.3 | 6.9 | 6.6 |  |  | 119 | 4 | 124 | 9 |  | 2016-03-04 | 2016-03-04 |  |  |  |  | 0.45 |  | 56 |  |  |  | Snow | 2016-03-04 | 2016-03-04 | 0.1065 | 0.1165 | 27.4215 | 35.605 | 1.03 | 2.48 | 10.7 | 11.3 | 4.06 |  |  |  |  | 460 | 59 | 118319 | [5 empty] | a. | Commercial | 4121600 | kilowatt hours |  | d. | Disposed By: |  |  | c. | Volatile Solids Content |  | % |  |  |  | 2016-03-04 | 89321.4 | 3002.4 | 93074.4 | 6755.4 | 95276.16 | 3202.56 | 99279.36 | 7205.76 | 119 | 4 | 124 | 9 | 0.1065 | 0.1165 | 27.4215 | 35.605 | 1.03 | 2.48 | 10.7 | 11.3 | 35.8 | 14.8 | 28662.912 | 11849.472 | 28506.7872 | 9047.232 | 2016-03-04 | 2016-03-13 | 2016-03-19 | 88 | 95 | 165 | 10 | 135 | 5 | 78 | 134100 | 9000 | 103800 | 4300 | 6 | 2016-03-04 | 2016-03-04 | [26 empty] | 0
Update EF area for Flow | 2016-03-05 | 2016-03-05 | 86 | 108 | 86 | 42 | 17 | 6.7 | 7.5 | 7 | 6.6 | 6.8 | 6.7 |  |  | 161 | 6 | 129 | 9 |  | 2016-03-05 | 2016-03-05 |  |  |  |  | 0.45 |  | 73 |  |  |  | Clear | 2016-03-05 | 2016-03-05 | 0.0535 | 0.07 | 30.869 | 38.91 | 1.2 | 2.68 | 9.7 | 10.6 | 4.68 |  |  |  |  | 350 | 59 | 116570 | [5 empty] | b. | Stand - by | 0 | kilowatt hours | [5 empty] | d. | Disposed By: | NYOFCO |  | pick one or more | inf no2 | ak | 2016-03-05 | 115475.64 | 4303.44 | 92523.96 | 6455.16 | 115475.64 | 4303.44 | 92523.96 | 6455.16 | 161 | 6 | 129 | 9 | 0.0535 | 0.07 | 30.869 | 38.91 | 1.2 | 2.68 | 9.7 | 10.6 | 39 | 14.5 | 27972.36 | 10399.98 | 27907.8084 | 7602.744 | 2016-03-05 | 2016-03-20 | 2016-03-26 | 89 | 90 | 145 | 9 | 157 | 5 | 30 | 109200 | 6700 | 117900 | 3700 | 7 | 2016-03-05 | 2016-03-05 | 87 | 91 | 130 | 99100 | 20 | 15600 | 151 | 114200 | 8 | 6100 | 91 |  | 12-Month Rolling |  |  | Current Month Average | [10 empty] | 0
& N 12-mon rolling avg | 2016-03-06 | 2016-03-06 | 86 | 108 | 86 | 44 | 17 | 6.7 | 7.5 | 6.9 | 6.4 | 7.1 | 6.8 |  |  | 160 | 6 | 140 | 10 |  | 2016-03-06 | 2016-03-06 |  |  |  |  | 0.46 |  | 144 |  |  |  | Clear | 2016-03-06 | 2016-03-06 | 0.064 | 0.092 | 30.756 | 39.17 | 1.11 | 2.08 | 9.6 | 11.1 | 4.31 |  |  | 4700 | 2560 | 390 | 59 | 97157 | [5 empty] | c. | Generated | 0 | kilowatt hours | [6 empty] | Tully, Wecare Organics, Coastal Distribution |  |  |  | inf no3 | al | 2016-03-06 | 114758.4 | 4303.44 | 100413.6 | 7172.4 | 114758.4 | 4303.44 | 100413.6 | 7172.4 | 160 | 6 | 140 | 10 | 0.064 | 0.092 | 30.756 | 39.17 | 1.11 | 2.08 | 9.6 | 11.1 | 39.3 | 14.3 | 28187.532 | 10256.532 | 28094.2908 | 7961.364 | 2016-03-06 | [13 empty] | 1 | 2016-03-06 | 2016-03-06 | [12 empty] | Average |  |  | 2016-03-01 | 2016-03-01 | [9 empty] | 0
| 2016-03-07 | 2016-03-07 | 84 | 110 | 84 | 32 | 17 | 6.6 | 7.2 | 6.9 | 6.5 | 6.8 | 6.6 |  |  | 108 | 5 | 145 | 10 |  | 2016-03-07 | 2016-03-07 |  |  |  |  | 0.46 |  | 88 |  |  | Influent HL & LL NO3 value < MDL, sustituted with zero | Clear | 2016-03-07 | 2016-03-07 | 0.1435 | 0 | 27.2735 | 36.795 | 1.2 | 1.47 | 11.7 | 12.3 | 3.75 |  |  | 3880 | 2620 | 270 | 59 | 100161 | [19 empty] | inf nh3 | am | 2016-03-07 | 75660.48 | 3502.8 | 101581.2 | 7005.6 | 75660.48 | 3502.8 | 101581.2 | 7005.6 | 108 | 5 | 145 | 10 | 0.1435 | 0 | 27.2735 | 36.795 | 1.2 | 1.47 | 11.7 | 12.3 | 36.9 | 15 | 25850.664 | 10508.4 | 25777.1052 | 8616.888 | 2016-03-07 | Maximum |  | 89 | 95 | 165 | 20 | 157 | 8 | 91 | 134000 | 16000 | 118000 | 6100 | 2 | 2016-03-07 | 2016-03-07 | [12 empty] | FLOW | 103 |  | FLOW | 91 | [9 empty] | 0
| 2016-03-08 | 2016-03-08 | 87 | 100 | 87 | 53 | 17 | 6.6 | 7.4 | 6.9 | 6.6 | 6.8 | 6.7 |  |  | 119 | 7 | 173 | 11 |  | 2016-03-08 | 2016-03-08 |  |  |  |  | 0.6 |  | 96 |  |  |  | Clear | 2016-03-08 | 2016-03-08 | 0.11 | 0.0195 | 30.309 | 40.175 | 1.05 | 2.28 | 13.4 | 13.4 | 3.69 | 210 |  | 3720 | 2980 | 250 | 59 | 132401 | [5 empty] | Amount of fuel consumed | [13 empty] | inf tkn | an | 2016-03-08 | 86344.02 | 5079.06 | 125525.34 | 7981.38 | 86344.02 | 5079.06 | 125525.34 | 7981.38 | 119 | 7 | 173 | 11 | 0.11 | 0.0195 | 30.309 | 40.175 | 1.05 | 2.28 | 13.4 | 13.4 | 40.3 | 16.7 | 29240.874 | 12117.186 | 29150.1765 | 9722.772 | 2016-03-08 | [13 empty] | 3 | 2016-03-08 | 2016-03-08 | [26 empty] | 0
Update DF22 to DL 27 | 2016-03-09 | 2016-03-09 | 92 | 112 | 92 | 54 | 18 | 6.5 | 7.5 | 6.9 | 6.4 | 6.6 | 6.5 |  |  | 151 | 4 | 165 | 7 |  | 2016-03-09 | 2016-03-09 |  |  |  |  | 0.42 |  | 53 |  |  |  | Clear | 2016-03-09 | 2016-03-09 | 0.04 | 0.083 | 28.9 | 39.505 | 0.97 | 2.76 | 10 | 10.5 | 4.42 |  |  | 4480 | 2780 | 270 | 59 | 117378 | [5 empty] | a. | Natural gas | 9787000 | cubic feet |  | Other Solid Wastes: | [10 empty] | 2016-03-09 | 115859.28 | 3069.12 | 126601.2 | 5370.96 | 115859.28 | 3069.12 | 126601.2 | 5370.96 | 151 | 4 | 165 | 7 | 0.04 | 0.083 | 28.9 | 39.505 | 0.97 | 2.76 | 10 | 10.5 | 39.6 | 14.2 | 30384.288 | 10895.376 | 30311.3964 | 8056.44 | 2016-03-09 |  |  | *** MANUALLY UPDATE DATA ONLY, NOT DATE INFO *** | [10 empty] | 4 | 2016-03-09 | 2016-03-09 | [26 empty] | 0
for 7-day avg | 2016-03-10 | 2016-03-10 | 90 | 111 | 90 | 64 | 18 | 6.6 | 7.2 | 6.8 | 6.5 | 6.7 | 6.6 |  |  | 177 | 6 | 154 | 8 |  | 2016-03-10 | 2016-03-10 |  |  |  |  | 0.41 |  | 98 |  |  | Influent HL & LL NO3 value < MDL, sustituted with zero | Clear | 2016-03-10 | 2016-03-10 | 0.1265 | 0 | 27.208 | 37.695 | 1.2 | 2.7 | 8.6 | 9.9 | 3.56 |  |  | 5080 | 3260 | 330 | 59 | 117360 | [5 empty] | b. | Oil | 254 | gallons |  | a. | Screenings | 4806 | cubic feet | [5 empty] | eff no2 | ao | 2016-03-10 | 132856.2 | 4503.6 | 115592.4 | 6004.8 | 132856.2 | 4503.6 | 115592.4 | 6004.8 | 177 | 6 | 154 | 8 | 0.1265 | 0 | 27.208 | 37.695 | 1.2 | 2.7 | 8.6 | 9.9 | 37.8 | 13.8 | 28372.68 | 10358.28 | 28293.867 | 7430.94 | 2016-03-10 | PREVIOUS MONTH'S DAILY DATA * |  |  | (FOR USE IN CURRENT MONTH'S 7-DAY MEANS) | [9 empty] | 5 | 2016-03-10 | 2016-03-10 | [26 empty] | 0
| 2016-03-11 | 2016-03-11 | 88 | 102 | 88 | 47 | 18 | 6.7 | 7.7 | 7 | 6.4 | 6.7 | 6.6 |  |  | 148 | 7 | 148 | 8 |  | 2016-03-11 | 2016-03-11 |  |  |  |  | 0.45 |  | 160 |  |  | Influent HL & LL NO3 value < MDL, sustituted with zero | Rain | 2016-03-11 | 2016-03-11 | 0.11 | 0 | 29.857 | 38.675 | 1.43 | 2.24 | 9 | 10.3 | 4.02 |  |  |  |  | 260 | 59 | 122653 | [5 empty] | c. | Gasoline | 0 | gallons |  | b. | Grit | 6966 | cubic feet | [5 empty] | eff no3 | ap | 2016-03-11 | 108620.16 | 5137.44 | 108620.16 | 5871.36 | 108620.16 | 5137.44 | 108620.16 | 5871.36 | 148 | 7 | 148 | 8 | 0.11 | 0 | 29.857 | 38.675 | 1.43 | 2.24 | 9 | 10.3 | 38.8 | 14 | 28476.096 | 10274.88 | 28384.356 | 7559.376 | 2016-03-11 | DAY | DATE | Dry Flow Avg | Total Flow Avg | TSS Inf Conc | TSS Eff Conc | CBOD Inf Conc | CBOD Eff Conc | Fecal Coliform | TSS Inf Load | TSS Eff Load | CBOD Inf Load | CBOD Eff Load | 6 | 2016-03-11 | 2016-03-11 | [26 empty] | 0
| 2016-03-12 | 2016-03-12 | 87 | 104 | 87 | 44 | 18 | 6.7 | 7.1 | 6.9 | 6.5 | 6.9 | 6.7 |  |  | 139 | 5 | 162 | 8 |  | 2016-03-12 | 2016-03-12 |  |  |  |  | 0.45 |  | 48 |  |  |  | Clear | 2016-03-12 | 2016-03-12 | 0.12 | 0.0195 | 30.635 | 38.75 | 1.45 | 1.73 | 9 | 10.1 | 4.96 |  |  |  |  | 280 | 59 | 119546 | [5 empty] | d. | Coal | 0 | tons |  | c. | Scum | 0 | cubic feet | [5 empty] | eff nh3 | aq | 2016-03-12 | 100855.62 | 3627.9 | 117543.96 | 5804.64 | 100855.62 | 3627.9 | 117543.96 | 5804.64 | 139 | 5 | 162 | 8 | 0.12 | 0.0195 | 30.635 | 38.75 | 1.45 | 1.73 | 9 | 10.1 | 38.9 | 13.3 | 28225.062 | 9650.214 | 28116.225 | 7328.358 | 2016-03-12 | 2016-02-24 | 2016-02-24 | 93 | 208 | 107 | 49 | 52 | 14 | 740 | 185615.04 | 85001.28 | 90205.44 | 24286.08 | 7 | 2016-03-12 | 2016-03-12 | 88 | 88 | 155 | 113700 | 9 | 6500 | 143 | 105000 | 6 | 4200 | 90 | [15 empty] | 0
| 2016-03-13 | 2016-03-13 | 87 | 106 | 87 | 44 | 18 | 6.3 | 7.2 | 6.8 | 6.6 | 6.9 | 6.7 |  |  | 155 | 5 | 181 | 8 |  | 2016-03-13 | 2016-03-13 |  |  |  |  | 0.44 |  | 104 |  |  |  | Clear | 2016-03-13 | 2016-03-13 | 0.05 | 0.0695 | 31.1365 | 41.81 | 1.27 | 3.04 | 7.9 | 9.5 | 3.96 |  |  | 2420 | 2640 | 260 | 59 | 118765 | [5 empty] | e. | Digester gas | 0 | cubic feet | [10 empty] | eff tkn | ar | 2016-03-13 | 112464.9 | 3627.9 | 131329.98 | 5804.64 | 112464.9 | 3627.9 | 131329.98 | 5804.64 | 155 | 5 | 181 | 8 | 0.05 | 0.0695 | 31.1365 | 41.81 | 1.27 | 3.04 | 7.9 | 9.5 | 41.9 | 13.8 | 30401.802 | 10013.004 | 30336.4998 | 6893.01 | 2016-03-13 | 2016-02-25 | 2016-02-25 | 99 | 102 | 84 | 12 | 137 | 6 | 20 | 71457.12 | 10208.16 | 116543.16 | 5104.08 | 1 | 2016-03-13 | 2016-03-13 | [12 empty] | NITROGEN LOADING - 12-MONTH ROLLING AVERAGE CALCULATION | [13 empty] | 0
| 2016-03-14 | 2016-03-14 | 89 | 236 | 136 | 46 | 16 | 6.8 | 7.6 | 7.1 | 6.5 | 6.8 | 6.6 |  |  | 91 | 11 | 223 | 24 |  | 2016-03-14 | 2016-03-14 |  |  |  |  | 0.51 | > | 4000 |  |  |  | Rain | 2016-03-14 | 2016-03-14 | 0.077 | 0.3955 | 17.9965 | 28.765 | 0.86 | 1.84 | 8.7 | 12 | 3.52 |  |  | 3960 | 2660 | 220 | 60 | 119969 | [5 empty] | f. | Propane | 0 | gallons | [12 empty] | 2016-03-14 | 67545.66 | 8164.86 | 165523.98 | 17814.24 | 103215.84 | 12476.64 | 252935.52 | 27221.76 | 91 | 11 | 223 | 24 | 0.077 | 0.3955 | 17.9965 | 28.765 | 0.86 | 1.84 | 8.7 | 12 | 29.2 | 14.7 | 33119.808 | 16673.328 | 32626.4136 | 13610.88 | 2016-03-14 | 2016-02-26 | 2016-02-26 | 86 | 86 | 186 | 7 | 146 | 3 | 91 | 133406.64 | 5020.68 | 104717.04 | 2151.72 | 2 | 2016-03-14 | 2016-03-14 | [26 empty] | 0
| 2016-03-15 | 2016-03-15 | 96 | 123 | 96 | 33 | 18 | 6.7 | 7.2 | 7 | 6.4 | 6.8 | 6.7 |  |  | 123 | 6 | 158 | 15 |  | 2016-03-15 | 2016-03-15 | 3.97 | 6.45 | 2.2195 | 3.32 | 0.45 |  | 156 |  | 100 |  | Clear | 2016-03-15 | 2016-03-15 | 0.2065 | 0.0275 | 20.774 | 33.06 | 1.39 | 2.54 | 7 | 9.8 | 4.26 | 1400 |  | 4160 | 2580 | 180 | 58 | 125245 | [10 empty] | Digester Gas Wasted (estimated) |  | 7064900 | cubic feet | [7 empty] | 2016-03-15 | 98478.72 | 4803.84 | 126501.12 | 12009.6 | 98478.72 | 4803.84 | 126501.12 | 12009.6 | 123 | 6 | 158 | 15 | 0.2065 | 0.0275 | 20.774 | 33.06 | 1.39 | 2.54 | 7 | 9.8 | 33.3 | 13.7 | 26661.312 | 10968.768 | 26469.1584 | 7846.272 | 2016-03-15 | 2016-02-27 | 2016-02-27 | 90 | 90 | 112 | 10 | 148 | 5 | 11 | 84067.2 | 7506 | 111088.8 | 3753 | 3 | 2016-03-15 | 2016-03-15 | [26 empty] | 0
| 2016-03-16 | 2016-03-16 | 86 | 103 | 86 | 54 | 19 | 6.7 | 7.3 | 7 | 6.4 | 6.9 | 6.6 |  |  | 135 | 3 | 150 | 6 |  | 2016-03-16 | 2016-03-16 |  |  |  |  | 0.46 |  | 30 |  |  |  | Rain | 2016-03-16 | 2016-03-16 | 0.098 | 0.0585 | 27.589 | 36.3445 | 1.5 | 3.11 | 8 | 8.6 | 4.42 |  |  | 3900 | 2860 | 220 | 58 | 134232 | TRUCKED WASTE RECEIVED THIS MONTH |  |  |  |  | Labor expended: | [15 empty] | 2016-03-16 | 96827.4 | 2151.72 | 107586 | 4303.44 | 96827.4 | 2151.72 | 107586 | 4303.44 | 135 | 3 | 150 | 6 | 0.098 | 0.0585 | 27.589 | 36.3445 | 1.5 | 3.11 | 8 | 8.6 | 36.5 | 13.2 | 26179.26 | 9467.568 | 26067.7292 | 6168.264 | 2016-03-16 | 2016-02-28 | 2016-02-28 | 91 | 91 | 133 | 14 | 169 | 6 | 49 | 100939.02 | 10625.16 | 128260.86 | 4553.64 | 4 | 2016-03-16 | 2016-03-16 | [26 empty] | 0
| 2016-03-17 | 2016-03-17 | 87 | 105 | 87 | 52 | 19 | 6.7 | 7.3 | 6.9 | 6.2 | 6.7 | 6.5 |  |  | 143 | 3 | 173 | 6 |  | 2016-03-17 | 2016-03-17 |  |  |  |  | 0.46 |  | 34 |  |  |  | Clear | 2016-03-17 | 2016-03-17 | 0.02 | 0.1095 | 30.5455 | 38.15 | 1.12 | 2.97 | 7.7 | 8.6 | 4.43 |  |  | 4460 | 3080 | 270 | 62 | 122703 | [5 empty] | Position |  |  |  | Number |  |  | Number | Total | [7 empty] | 2016-03-17 | 103757.94 | 2176.74 | 125525.34 | 4353.48 | 103757.94 | 2176.74 | 125525.34 | 4353.48 | 143 | 3 | 173 | 6 | 0.02 | 0.1095 | 30.5455 | 38.15 | 1.12 | 2.97 | 7.7 | 8.6 | 38.3 | 12.7 | 27789.714 | 9214.866 | 27680.877 | 6239.988 | 2016-03-17 | 2016-02-29 | 2016-02-29 | 92 | 92 | 146 | 9 | 145 | 5 | 204 | 112022.88 | 6905.52 | 111255.6 | 3836.4 | 5 | 2016-03-17 | 2016-03-17 | [13 empty] | 11300 | 11300 | 11300 | 11300 | 11300 | 11300 | 11300 | 11300 | 11300 | 11300 | 11300 | 11300 |  | 0
| 2016-03-18 | 2016-03-18 | 84 | 95 | 84 | 44 | 18 | 6.7 | 7.3 | 6.9 | 6.1 | 6.6 | 6.4 |  |  | 144 | 3 | 137 | 7 |  | 2016-03-18 | 2016-03-18 |  |  |  |  | 0.47 |  | 38 |  |  |  | Clear | 2016-03-18 | 2016-03-18 | 0.02 | 0.0995 | 28.577 | 38.69 | 1.24 | 3.39 | 7.7 | 8.5 | 4.23 |  |  |  |  | 250 | 62 | 126171 | 1. Septage, holding tank waste and |  |  |  |  | Name |  |  |  | Full Time |  |  | Part Time | hours per week | [7 empty] | 2016-03-18 | 100880.64 | 2101.68 | 95976.72 | 4903.92 | 100880.64 | 2101.68 | 95976.72 | 4903.92 | 144 | 3 | 137 | 7 | 0.02 | 0.0995 | 28.577 | 38.69 | 1.24 | 3.39 | 7.7 | 8.5 | 38.8 | 13.1 | 27181.728 | 9177.336 | 27104.6664 | 5954.76 | 2016-03-18 | Average |  | 93 | 112 | 125 | 14 | 121 | 7 | 86 |  |  |  |  | 6 | 2016-03-18 | 2016-03-18 | [12 empty] | *** MANUALLY UPDATE *** | [13 empty] | 0
| 2016-03-19 | 2016-03-19 | 87 | 110 | 87 | 44 | 18 | 6.5 | 6.9 | 6.7 | 6.3 | 6.8 | 6.5 |  |  | 153 | 4 | 136 | 6 |  | 2016-03-19 | 2016-03-19 |  |  |  |  | 0.45 |  | 7 |  |  | Influent HL & LL NO2 value < MDL, sustituted with zero | Clear | 2016-03-19 | 2016-03-19 | 0 | 0.1095 | 31.584 | 41.135 | 1.1 | 2.89 | 8.2 | 8.8 | 4.42 |  |  |  |  | 270 | 62 | 125708 | portable toilet waste |  |  |  |  | SSEE | [5 empty] | 3 | 0 | 120 | [7 empty] | 2016-03-19 | 111013.74 | 2902.32 | 98678.88 | 4353.48 | 111013.74 | 2902.32 | 98678.88 | 4353.48 | 153 | 4 | 136 | 6 | 0 | 0.1095 | 31.584 | 41.135 | 1.1 | 2.89 | 8.2 | 8.8 | 41.2 | 12.8 | 29893.896 | 9287.424 | 29846.7333 | 6385.104 | 2016-03-19 |  |  | {PASTE AS VALUE, PREVIOUS MONTHS DATA, see note in cell DD42} | [10 empty] | 7 | 2016-03-19 | 2016-03-19 | 88 | 95 | 165 | 134100 | 10 | 9000 | 135 | 103800 | 5 | 4300 | 78 |  | MONTH | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 |  | 0
| 2016-03-20 | 2016-03-20 | 94 | 118 | 94 | 42 | 18 | 6.6 | 7.5 | 6.8 | 6.4 | 6.6 | 6.5 |  |  | 182 | 4 | 129 | 8 |  | 2016-03-20 | 2016-03-20 |  |  |  |  | 0.4 |  | 4 |  |  | Influent HL & LL NO2 value < MDL, sustituted with zero | Snow | 2016-03-20 | 2016-03-20 | 0 | 0.103 | 31.1335 | 39.38 | 1.09 | 2.45 | 9.3 | 10.1 | 4.24 |  |  | 4960 | 2860 | 260 | 63 | 74975 |  |  | Total | Max. day |  | SEE | [5 empty] | 5 | 0 | 200 | [7 empty] | 2016-03-20 | 142680.72 | 3135.84 | 101130.84 | 6271.68 | 142680.72 | 3135.84 | 101130.84 | 6271.68 | 182 | 4 | 129 | 8 | 0 | 0.103 | 31.1335 | 39.38 | 1.09 | 2.45 | 9.3 | 10.1 | 39.5 | 13.6 | 30966.42 | 10661.856 | 30872.3448 | 7917.996 | 2016-03-20 | [13 empty] | 1 | 2016-03-20 | 2016-03-20 | [12 empty] | TN | 15028.5186 | 14670 | 10391.7745 | 11924.8934 | 10200.385 | 10248.9426 | 9299.99 | 9330.6844 | 11907.94 | 9500.63 | 10577.82 | 12335.34 |  | 0
| 2016-03-21 | 2016-03-21 | 94 | 121 | 100 | 50 | 18 | 6.6 | 7.2 | 6.8 | 6.4 | 6.7 | 6.6 |  |  | 124 | 6 | 144 | 10 |  | 2016-03-21 | 2016-03-21 |  |  |  |  | 0.46 |  | 38 |  |  |  | Snow/Clear | 2016-03-21 | 2016-03-21 | 0.0235 | 0.1195 | 27.939 | 37.26 | 1 | 1.85 | 9.4 | 10 | 3.62 |  |  | 4580 | 3460 | 340 | 63 | 141476 | Volume (gallons) |  | 1049010 | 72750 |  | Oiler | [5 empty] | 2 | 0 | 80 | [7 empty] | 2016-03-21 | 97211.04 | 4703.76 | 112890.24 | 7839.6 | 103416 | 5004 | 120096 | 8340 | 124 | 6 | 144 | 10 | 0.0235 | 0.1195 | 27.939 | 37.26 | 1 | 1.85 | 9.4 | 10 | 37.4 | 12.9 | 31191.6 | 10758.6 | 31074.84 | 8340 | 2016-03-21 | CURRENT MONTH'S DAILY DATA |  |  | (FOR USE IN NEXT MONTH'S 7-DAY FLOW WEIGHTED MEANS) | [9 empty] | 2 | 2016-03-21 | 2016-03-21 | [12 empty] | Do NOT "move" the months - just update the year and the NITROGEN LOADING for the current month. | [13 empty] | 0
| 2016-03-22 | 2016-03-22 | 93 | 149 | 93 | 49 | 18 | 6.4 | 7.3 | 6.8 | 6.4 | 6.7 | 6.6 |  |  | 166 | 5 | 142 | 9 |  | 2016-03-22 | 2016-03-22 |  |  |  |  | 0.45 |  | 13 |  |  | Influent HL NO2 value < MDL, sustituted with zero | Clear | 2016-03-22 | 2016-03-22 | 0.0035 | 0.1195 | 31.775 | 40.34 | 1.34 | 2.52 | 7 | 8.4 | 4.03 | 150 |  | 4660 | 3700 | 350 | 61 | 121881 | [5 empty] | SSTW | [5 empty] | 12 | 0 | 480 | [7 empty] | 2016-03-22 | 128752.92 | 3878.1 | 110138.04 | 6980.58 | 128752.92 | 3878.1 | 110138.04 | 6980.58 | 166 | 5 | 142 | 9 | 0.0035 | 0.1195 | 31.775 | 40.34 | 1.34 | 2.52 | 7 | 8.4 | 40.5 | 12.3 | 31412.61 | 9540.126 | 31288.5108 | 6515.208 | 2016-03-22 | DAY | DATE | Dry Flow Avg | Total Flow Avg | TSS Inf Conc | TSS Eff Conc | CBOD Inf Conc | CBOD Eff Conc | Fecal Coliform | TSS Inf Load | TSS Eff Load | CBOD Inf Load | CBOD Eff Load | 3 | 2016-03-22 | 2016-03-22 | [12 empty] | e.g. for April 2003 - replace "APR 02" with "APR 03" in cell EK29, and manually COPY & PASTE RANGE VALUE the nitrogen from cell EK36 into cell EK30 | [13 empty] | 0
| 2016-03-23 | 2016-03-23 | 93 | 113 | 93 | 57 | 19 | 6.3 | 7.2 | 6.7 | 6.4 | 6.6 | 6.5 |  |  | 162 | 6 | 163 | 9 |  | 2016-03-23 | 2016-03-23 |  |  |  |  | 0.5 |  | 37 |  |  | Influent HL & LL NO2 value < MDL, sustituted with zero | Clear | 2016-03-23 | 2016-03-23 | 0 | 0.106 | 32.031 | 39.09 | 1.09 | 2.2 | 8.1 | 8.7 | 3.93 |  |  | 4980 | 3300 | 310 | 61 | 150362 | 2. All other |  |  |  |  | STW | [5 empty] | 40 | 0 | 1600 | [7 empty] | 2016-03-23 | 125650.44 | 4653.72 | 126426.06 | 6980.58 | 125650.44 | 4653.72 | 126426.06 | 6980.58 | 162 | 6 | 163 | 9 | 0 | 0.106 | 32.031 | 39.09 | 1.09 | 2.2 | 8.1 | 8.7 | 39.2 | 12 | 30404.304 | 9307.44 | 30318.9858 | 6747.894 | 2016-03-23 | 2016-03-26 | 2016-03-26 | 83 | 83 | 146 | 9 | 134 | 4 | 58 | 101064.12 | 6229.98 | 92757.48 | 2768.88 | 4 | 2016-03-23 | 2016-03-23 | [26 empty] | 0
| 2016-03-24 | 2016-03-24 | 84 | 105 | 84 | 48 | 18 | 6.5 | 7.6 | 6.9 | 6.2 | 6.6 | 6.5 |  |  | 175 | 5 | 137 | 8 |  | 2016-03-24 | 2016-03-24 |  |  |  |  | 0.44 |  | 117 |  |  | Influent HL & LL NO2 value < MDL, sustituted with zero | Clear | 2016-03-24 | 2016-03-24 | 0 | 0.1025 | 31.7635 | 39.675 | 1.43 | 2.65 | 6.8 | 7.5 | 3.94 |  |  | 3880 | 2920 | 330 | 61 | 112120 | types of wastes |  |  |  |  | Clerical | [5 empty] | 1 | 0 | 35 | [7 empty] | 2016-03-24 | 122598 | 3502.8 | 95976.72 | 5604.48 | 122598 | 3502.8 | 95976.72 | 5604.48 | 175 | 5 | 137 | 8 | 0 | 0.1025 | 31.7635 | 39.675 | 1.43 | 2.65 | 6.8 | 7.5 | 39.8 | 11.6 | 27882.288 | 8126.496 | 27794.718 | 5254.2 | 2016-03-24 | 2016-03-27 | 2016-03-27 | 85 | 85 | 140 | 9 | 158 | 5 | 63 | 99246 | 6380.1 | 112006.2 | 3544.5 | 5 | 2016-03-24 | 2016-03-24 | [12 empty] | 12-Month Rolling |  |  | Current Month Average | [10 empty] | 0
| 2016-03-25 | 2016-03-25 | 84 | 136 | 85 | 36 | 18 | 6.4 | 7.1 | 6.7 | 6.3 | 6.6 | 6.5 |  |  | 154 | 4 | 155 | 9 |  | 2016-03-25 | 2016-03-25 |  |  |  |  | 0.44 |  | 40 |  |  | Influent HL & LL NO2 value < MDL, sustituted with zero | Rain | 2016-03-25 | 2016-03-25 | 0 | 0.086 | 29.577 | 39.48 | 1.14 | 2.16 | 8.1 | 9 | 4.05 |  |  |  |  | 460 | 61 | 128535 |  |  | Total | Max. day | [17 empty] | 2016-03-25 | 107886.24 | 2802.24 | 108586.8 | 6305.04 | 109170.6 | 2835.6 | 109879.5 | 6380.1 | 154 | 4 | 155 | 9 | 0 | 0.086 | 29.577 | 39.48 | 1.14 | 2.16 | 8.1 | 9 | 39.6 | 12.3 | 28072.44 | 8719.47 | 27987.372 | 6380.1 | 2016-03-25 | 2016-03-28 | 2016-03-28 | 85 | 131 | 175 | 34 | 71 | 11 | 4000 | 191194.5 | 37146.36 | 77570.34 | 12017.94 | 6 | 2016-03-25 | 2016-03-25 | [12 empty] | Average |  |  | Effluent | 2016-03-01 | [9 empty] | 0
| 2016-03-26 | 2016-03-26 | 83 | 108 | 83 | 55 | 19 | 6.6 | 7 | 6.8 | 6.4 | 6.6 | 6.5 |  |  | 134 | 4 | 146 | 9 |  | 2016-03-26 | 2016-03-26 |  |  |  |  | 0.46 |  | 58 |  |  |  | Clear | 2016-03-26 | 2016-03-26 | 0.03 | 0.073 | 31.627 | 40.57 | 1.19 | 1.88 | 9.9 | 10.2 | 4.28 |  |  |  |  | 540 | 60 | 127939 | Volume (gallons) | [20 empty] | 2016-03-26 | 92757.48 | 2768.88 | 101064.12 | 6229.98 | 92757.48 | 2768.88 | 101064.12 | 6229.98 | 134 | 4 | 146 | 9 | 0.03 | 0.073 | 31.627 | 40.57 | 1.19 | 1.88 | 9.9 | 10.2 | 40.7 | 13.3 | 28173.354 | 9206.526 | 28083.3654 | 7060.644 | 2016-03-26 | 2016-03-29 | 2016-03-29 | 82 | 82 | 149 | 7 | 141 | 3 | 120 | 101898.12 | 4787.16 | 96427.08 | 2051.64 | 7 | 2016-03-26 | 2016-03-26 | 89 | 90 | 145 | 109200 | 9 | 6700 | 157 | 117900 | 5 | 3700 | 30 |  | N Loading | 11300 |  | N Loading | 10391.7745 | [9 empty] | 0
| 2016-03-27 | 2016-03-27 | 85 | 109 | 85 | 60 | 18 | 6.6 | 7.3 | 7 | 6.6 | 7.1 | 6.9 |  |  | 158 | 5 | 140 | 9 |  | 2016-03-27 | 2016-03-27 |  |  |  |  | 0.44 |  | 63 |  |  |  | Clear | 2016-03-27 | 2016-03-27 | 0.027 | 0.053 | 30.959 | 39.05 | 1.02 | 2.64 | 7.6 | 7.8 | 3.79 |  |  | 2980 | 2800 | 520 | 60 | 129075 | [5 empty] | Hours per week are straight hours only, and do not include any overtime or compensatory time. | [15 empty] | 2016-03-27 | 112006.2 | 3544.5 | 99246 | 6380.1 | 112006.2 | 3544.5 | 99246 | 6380.1 | 158 | 5 | 140 | 9 | 0.027 | 0.053 | 30.959 | 39.05 | 1.02 | 2.64 | 7.6 | 7.8 | 39.1 | 11.5 | 27717.99 | 8152.35 | 27682.545 | 5529.42 | 2016-03-27 | 2016-03-30 | 2016-03-30 | 83 | 83 | 140 | 6 | 145 | 2 | 9 | 96910.8 | 4153.32 | 100371.9 | 1384.44 | 1 | 2016-03-27 | 2016-03-27 | [26 empty] | 0
| 2016-03-28 | 2016-03-28 | 85 | 200 | 131 | 53 | 17 | 6.6 | 7.2 | 6.9 | 6.1 | 7 | 6.5 |  |  | 71 | 11 | 175 | 34 |  | 2016-03-28 | 2016-03-28 |  |  |  |  | 0.47 | > | 4000 |  |  |  | Rain | 2016-03-28 | 2016-03-28 | 0.0925 | 0.305 | 17.7975 | 27.11 | 0.96 | 2 | 6.9 | 9.8 | 2.47 |  |  | 4060 | 3060 | 410 | 60 | 125528 | 3. Number of Part 364 haulers currently | [20 empty] | 2016-03-28 | 50331.9 | 7797.9 | 124057.5 | 24102.6 | 77570.34 | 12017.94 | 191194.5 | 37146.36 | 71 | 11 | 175 | 34 | 0.0925 | 0.305 | 17.7975 | 27.11 | 0.96 | 2 | 6.9 | 9.8 | 27.5 | 12.8 | 30044.85 | 13984.512 | 29618.7594 | 10706.892 | 2016-03-28 | 2016-03-31 | 2016-03-31 | 82 | 82 | 124 | 6 | 150 | 3 | 18 | 84801.12 | 4103.28 | 102582 | 2051.64 | 2 | 2016-03-28 | 2016-03-28 | [26 empty] | 0
| 2016-03-29 | 2016-03-29 | 82 | 94 | 82 | 57 | 18 | 6.7 | 7.2 | 7 | 6.4 | 6.9 | 6.6 |  |  | 141 | 3 | 149 | 7 |  | 2016-03-29 | 2016-03-29 |  |  |  |  | 0.43 |  | 120 |  |  |  | Clear | 2016-03-29 | 2016-03-29 | 0.1365 | 0.076 | 28.0565 | 39.335 | 1.44 | 3.06 | 5.3 | 6.5 | 4.41 | 140 |  | 4680 | 3240 | 500 | 59 | 129401 | approved to transport wastes to this | [20 empty] | 2016-03-29 | 96427.08 | 2051.64 | 101898.12 | 4787.16 | 96427.08 | 2051.64 | 101898.12 | 4787.16 | 141 | 3 | 149 | 7 | 0.1365 | 0.076 | 28.0565 | 39.335 | 1.44 | 3.06 | 5.3 | 6.5 | 39.5 | 11 | 27013.26 | 7522.68 | 26900.4198 | 4445.22 | 2016-03-29 | Average |  | 87 | 91 | 149 | 12 | 144 | 6 | 67 |  |  |  |  | 3 | 2016-03-29 | 2016-03-29 | [12 empty] | Actual 12-Month Rolling Average | [13 empty] | 0
| 2016-03-30 | 2016-03-30 | 83 | 105 | 83 | 54 | 17 | 6.6 | 7.3 | 6.8 | 6.2 | 6.8 | 6.5 |  |  | 145 | 2 | 140 | 6 |  | 2016-03-30 | 2016-03-30 |  |  |  |  | 0.43 |  | 9 |  |  |  | Clear | 2016-03-30 | 2016-03-30 | 0.1505 | 0.013 | 30.164 | 39.365 | 1.94 | 3.32 | 4.7 | 6.1 | 4.38 |  |  | 4300 | 3440 | 450 | 59 | 143472 | POTW | [20 empty] | 2016-03-30 | 100371.9 | 1384.44 | 96910.8 | 4153.32 | 100371.9 | 1384.44 | 96910.8 | 4153.32 | 145 | 2 | 140 | 6 | 0.1505 | 0.013 | 30.164 | 39.365 | 1.94 | 3.32 | 4.7 | 6.1 | 39.5 | 11.4 | 27342.69 | 7891.308 | 27249.2403 | 4222.542 | 2016-03-30 | [13 empty] | 4 | 2016-03-30 | 2016-03-30 | [12 empty] | MONTH | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01 |  | 0
| 2016-03-31 | 2016-03-31 | 82 | 99 | 82 | 50 | 19 | 6.5 | 7.3 | 6.8 | 6.1 | 6.6 | 6.4 |  |  | 150 | 3 | 124 | 6 |  | 2016-03-31 | 2016-03-31 |  |  |  |  | 0.42 |  | 18 |  |  |  | Clear | 2016-03-31 | 2016-03-31 | 0.02 | 0.0825 | 30.8645 | 37.78 | 1.51 | 3.53 | 5.5 | 6.4 | 4.46 |  |  | 4380 | 3500 | 390 | 58 | 136718 | a. Septage, etc. |  | 25 |  |  | I hearby affirm under penalty of perjury that information provided on this form is true to the best of my knowledge and belief. False statements | [15 empty] | 2016-03-31 | 102582 | 2051.64 | 84801.12 | 4103.28 | 102582 | 2051.64 | 84801.12 | 4103.28 | 150 | 3 | 124 | 6 | 0.02 | 0.0825 | 30.8645 | 37.78 | 1.51 | 3.53 | 5.5 | 6.4 | 37.9 | 11.4 | 25919.052 | 7796.232 | 25836.9864 | 4376.832 | 2016-03-31 | [13 empty] | 5 | 2016-03-31 | 2016-03-31 | [12 empty] | TKN | 30331.8738 | 29340.8102 | 28412.3063 | [10 empty] | 0
| Permitted |  | Monthly | Monthly | Monthly |  | Average | Minimum | 6.3 |  | Minimum | 6.1 |  | Monthly | Monthly | 30-day arithmetic mean (1) |  | 30-day arithmetic mean (1) |  |  |  |  | 30-day arithmetic mean (1) |  | 30-day arithmetic mean (1) |  | Average | 30 day Geometric |  | Daily Maximum |  | 2/29/2016: DO Control O/S, Contingency Sampling - DO |  | 30-Day Means |  | 0.07 | 0.1 | 28.5 | 37.7 | 1.19 | 2.55 | 8.7 | 9.9 | 2.47 | 1400 | [6 empty] | b. All others |  |  |  |  | made herein are punishable as a Class A misdemeanor pursuant to Section 210.45 of the Penal Law. | [15 empty] | Avg | 104300 | 4200 | 108500 | 8800 | 107600 | 4500 | 114600 | 9800 | 144 | 6 | 149 | 12 | 0.1 | 0.1 | 28.5 | 37.7 | 1.19 | 2.6 | 8.7 | 9.9 | 37.9 | 13.6 | 28540.0988 | 10391.7745 | 28412.3063 | 7569.3302 | Eff use for further calculations (e.g. 12-month rolling average) | * To update Section entitled "Previous Month's Daily Data" when starting sheet for a new month, i.e. April 2003: | [40 empty] | TOTAL | 0
| Flow |  | Average | Maximum | Average |  | 18 | Maximum | 7.7 |  | Maximum | 7.4 |  | Maximum | Maximum | Influent | Effluent | Influent | Effluent |  |  |  | Influent | Effluent | Influent | Effluent | 0.45806 | Mean (1) |  |  |  | 3/7/2016: DO Control O/S, Contingency Sampling - DO |  | See (1) |  | Arithmetic Means (mg/L) |  |  |  | Arithmetic Means (mg/L) |  |  |  | Minimum | Maximum | [28 empty] | 30-Day Flow Weighting with Dry Flow |  |  |  | 30-Day Flow Weighting with Total Flow |  |  |  | 30-day arithmetic mean {w/o wet weather conc.} |  |  |  | Nitrogen Average (mg/L) | [8 empty] | Rounded | 28500 | 10400 | 28400 | 7600 | Eff use for reporting (e.g. DMR, Tab, Nutrients) |  | 1. Open previous month's file, i.e. March 2003
| 150 |  | 87 | 236 | 91 |  | Maximum | of Instantaneous Samples |  |  | of Instantaneous Samples |  |  |  |  | 144 | 6 | 149 | 12 |  |  |  | 4.3 | 4 | 2.4 | 2.3 | Maximum |  | 67 |  | 100 | 3/14/2016: DO Control O/S, Contingency Sampling - DO |  | 30 Day Average | [9 empty] | 4.1 | 400 | [28 empty] | CBOD Inf | CBOD Eff | TSS Inf | TSS Eff | CBOD Inf | CBOD Eff | TSS Inf | TSS Eff | % Removal | 96% | % Removal | 92% | 0.2 | 0.4 | 32 | 41.8 | 1.94 | 3.5 | 13.4 | 16.2 | 41.9 | 19.8 | 33119.808 | 16673.328 |  |  |  |  | 2. Highlight and copy cells DF33 to DP39 ( "Current Month's Daily Data" table of March 2003 file), | [26 empty] | 12-Month Rolling |  |  | Current Month Average
[5 empty] | 12-Month Rolling |  | 19 | [8 empty] | % Removal | 96% | % Removal | 92% | [7 empty] | 0.6 |  |  |  |  | 3/21/2016: DO Control O/S, Contingency Sampling - DO |  | Quantitative | [5 empty] | Total Nitrogen | 10400 |  |  | Average | Average | [28 empty] | 144 | 6 | 149 | 12 | 141 | 6 | 151 | 13 | Inf. CBOD | Eff. CBOD | Inf. TSS | Eff. TSS | Nitrogen Max (mg/L) | [8 empty] | Rounded | 33100 | 16700 |  |  |  |  | 3. Paste as Values to new month's file (April 2003) in cells DF22 to DP28 ("Previous Month's Daily Data" table) | [26 empty] | Average |  |  | Influent | 2016-03-01
[5 empty] | 103 |  |  | 30-Day Average Effluent Loading (1) | [7 empty] | 4500 | lbs/day | 9800 | lbs/day | [14 empty] | Discharge Loading | [5 empty] | Effluent | lbs/day | [32 empty] | 30-Day Arithmetic Means |  |  |  | Daily Maximum load. |  |  |  | With wet weather concentrations: | [10 empty] | 1-15th | 37.2667 | 14.9467 | 59.89% | [32 empty] | N Loading | 29400 |  | TKN Loading | 28412.3063
| (1) Refer to January 1994 edition of DMR Manual for Completing the Discharge Monitoring Report for the National Pollution Discharge Elimination System (NPDES), for procedures to calculate loadings, means, maximum, minimum, percent removal, etc. | [19 empty] | (1) Refer to January 1994 edition of DMR Manual for Completing the Discharge Monitoring Report for the National Pollution Discharge Elimination System (NPDES), for procedures to calculate loadings, means, maximum, minimum, percent removal, etc. | [12 empty] | (1) Refer to January 1994 edition of DMR Manual for Completing the Discharge Monitoring Report for the National Pollution Discharge Elimination System (NPDES), for procedures to calculate loadings, means, maximum, minimum, percent removal, etc. | [22 empty] | Signature of Chief Operator or Designated Facility Representative. | [7 empty] | Date | [8 empty] | CBOD Inf | CBOD Eff | TSS Inf | TSS Eff | CBOD Inf | CBOD Eff | TSS Inf | TSS Eff | % Removal | 96% | % Removal | 92% | [7 empty] | 16-31th | 38.4375 | 12.3688 | 67.82% | [18 empty] | DAY | DATE | Dry Flow Avg | Total Flow Avg | TSS Inf Conc | TSS Inf Load | TSS Eff Conc | Total TSS lbs | CBOD Inf Conc | CBOD Inf Load | CBOD Eff Conc | Total CBOD lbs | Fecal Coliform
| (2) If temperature is measured more than once a day, report the average for the day. | [19 empty] | (2) If temperature is measured more than once a day, report the average for the day. | [12 empty] | (2) If temperature is measured more than once a day, report the average for the day. | [39 empty] | 144 | 6 | 149 | 12 | 142700 | 17200 | 252900 | 58800 | 144 | 6 | 149 | 12 | [29 empty] | 2016-02-24 | 2016-02-24 | 93 | 208 | 107 | 185615.04 | 49 | 85001.28 | 52 | 90205.44 | 14 | 24286.08 | 740
| NOTE: Refer to current SPDES permit for specific monitoring requirements. Sample type for temperature, pH and settleable solids is grab. | [19 empty] | NOTE: Refer to current SPDES permit for specific monitoring requirements. Sample type for temperature, pH and settleable solids is grab. | [12 empty] | NOTE: Refer to current SPDES permit for specific monitoring requirements. Sample type for temperature, pH and settleable solids is grab. | [43 empty] | Daily Maximum conc. | [36 empty] | 2016-02-25 | 2016-02-25 | 99 | 102 | 84 | 71457.12 | 12 | 10208.16 | 137 | 116543.16 | 6 | 5104.08 | 20 |  | Actual 12-Month Rolling Average
[78 empty] | 182 | 21 | 223 | 72 | [33 empty] | 2016-02-26 | 2016-02-26 | 86 | 86 | 186 | 133406.64 | 7 | 5020.68 | 146 | 104717.04 | 3 | 2151.72 | 91 |  | MONTH | 2016-01-01 | 2016-02-01 | 2016-03-01 | 2015-04-01 | 2015-05-01 | 2015-06-01 | 2015-07-01 | 2015-08-01 | 2015-09-01 | 2015-10-01 | 2015-11-01 | 2015-12-01
[16 empty] | COD |  | TSS | [15 empty] | Date of Sample | Arsenic | Cadmium | Chromium | Copper | Lead | Nickel | Silver | Zinc | Cyanide | Mercury | [26 empty] | LOADING CALCULATIONS DONE HERE FOR: | [13 empty] | Rounded Avg | 100 | 100 | 21400 | 28400 | 900 | 1900 | 6600 | 7600 | [21 empty] | 2016-02-27 | 2016-02-27 | 90 | 90 | 112 | 84067.2 | 10 | 7506 | 148 | 111088.8 | 5 | 3753 | 11 |  | Chlorides | 530 | 1140 | 400
[15 empty] | Date | Influent | Effluent | Influent | Effluent | [15 empty] | Effluent Conc. | Effluent Conc. | Effluent Conc. | Effluent Conc. | Effluent Conc. | Effluent Conc. | Effluent Conc. | Effluent Conc. | Effluent Conc. | Effluent Conc. | [7 empty] | Septage Hauler Accepting Plants: HP, 26, OB | [18 empty] | PHOSPHORUS / ORTHOPHOSPHATE / CHLORINE RESIDUAL | [14 empty] | Influent (lb/d) |  |  |  | Effluent (lb/d) | [24 empty] | 2016-02-28 | 2016-02-28 | 91 | 91 | 133 | 100939.02 | 14 | 10625.16 | 169 | 128260.86 | 6 | 4553.64 | 49
[15 empty] | 1-15th | 140.8667 | 7.0667 | 152.1333 | 15.0667 | [15 empty] | ug/l | ug/l | ug/l | ug/L | ug/l | ug/l | ug/l | ug/l | ug/L | ng/L | [7 empty] | 3. Number of Part 364 haulers currently |  |  |  | And fill in Part 1, total and max | [28 empty] | Day | NO2 | NO3 | NH3 | TKN | NO2 | NO3 | NH3 | TKN | 64.12% | % TN Removal | [19 empty] | 2016-02-29 | 2016-02-29 | 92 | 92 | 146 | 112022.88 | 9 | 6905.52 | 145 | 111255.6 | 5 | 3836.4 | 204
[15 empty] | 16-31th | 146.0625 | 4.4375 | 146.25 | 9.3125 | [14 empty] | 2016-03-14 | 0.5 | 0.046 | 0.58 | 7.6 | 0.6 | 3.4 | 0.031 | 48.3 | 11.5 | 4.18 | [7 empty] | approved to transport wastes to this | [19 empty] | INFLUENT |  |  |  | EFFLUENT |  |  |  | EFFLUENT |  |  |  |  | 2016-03-01 | 31.3584 | 114.4582 | 21644.3516 | 29320.104 | 650.6868 | 2195.088 | 9250.728 | 9485.916 | [21 empty] | 2016-03-01 | 2016-03-01 | 86 | 94 | 119 | 93291.24 | 7 | 5487.72 | 146 | 114458.16 | 5 | 3919.8 | 128 |  | 12-Month Rolling |  |  | Current Month Average
[15 empty] | Removal | 1-15th | 94.98% | 1-15th | 90.1% | [32 empty] | POTW | [19 empty] | PHOS. | PHOS. | ORTHO. | ORTHO. | PHOS. | PHOS. | ORTHO. | ORTHO. | CL RES. | CL RES. |  |  |  | 2016-03-02 | 95.2178 | 196.1568 | 18106.9073 | 25708.8006 | 702.8952 | 2231.2836 | 9235.716 | 13240.584 | [21 empty] | 2016-03-02 | 2016-03-02 | 85 | 98 | 128 | 104616.96 | 72 | 58847.04 | 138 | 112790.16 | 21 | 17163.72 | 92 |  | Average |  |  | Influent | 2016-03-01
[16 empty] | 16-31th | 96.96% | 16-31th | 93.63% | [32 empty] | a. Septage, etc. |  | put below number here | [16 empty] | Day | mg/L | lb/d | mg/L | lb/d | mg/L | lb/d | mg/L | lb/d | mg/L | lb/d |  |  |  | 2016-03-03 | 84.1172 | 86.1689 | 19620.5172 | 26370.4128 | 724.9128 | 2113.1892 | 7385.904 | 8001.396 | [21 empty] | 2016-03-03 | 2016-03-03 | 82 | 82 | 133 | 90956.04 | 20 | 13677.6 | 178 | 121730.64 | 8 | 5471.04 | 109 |  | Chlorides | 690 |  | Chlorides | 400
[52 empty] | b. All others | [18 empty] | 2016-03-01 | 4.5445 | 3562.7062 | 2.635 | 2065.7346 | 1.49 | 1168.1004 | 1.27 | 995.6292 | 0.44 | 344.9424 |  |  |  | 2016-03-04 | 85.2682 | 93.2746 | 21954.7498 | 28506.7872 | 824.6592 | 1985.5872 | 8566.848 | 9047.232 | [21 empty] | 2016-03-04 | 2016-03-04 | 90 | 96 | 124 | 99279.36 | 9 | 7205.76 | 119 | 95276.16 | 4 | 3202.56 | 56
[49 empty] | If you are NR or PR - replace this in cells AY50 and AY118: | [21 empty] | 2016-03-02 | [8 empty] | 0.43 | 351.4476 |  |  |  | 2016-03-05 | 38.3723 | 50.2068 | 22140.4816 | 27907.8084 | 860.688 | 1922.2032 | 6957.228 | 7602.744 | [21 empty] | 2016-03-05 | 2016-03-05 | 86 | 86 | 129 | 92523.96 | 9 | 6455.16 | 161 | 115475.64 | 6 | 4303.44 | 73 | Is Nitrogen updated?
[71 empty] | 2016-03-03 | [8 empty] | 0.6 | 410.328 |  |  |  | 2016-03-06 | 45.9034 | 65.9861 | 22059.4334 | 28094.2908 | 796.1364 | 1491.8592 | 6885.504 | 7961.364 | [21 empty] | 2016-03-06 | 2016-03-06 | 86 | 86 | 140 | 100413.6 | 10 | 7172.4 | 160 | 114758.4 | 6 | 4303.44 | 144
[50 empty] | Lead | Nickel | [19 empty] | 2016-03-04 | [8 empty] | 0.45 | 360.288 |  |  |  | 2016-03-07 | 100.5304 | 0 | 19106.7232 | 25777.1052 | 840.672 | 1029.8232 | 8196.552 | 8616.888 | [21 empty] | 2016-03-07 | 2016-03-07 | 84 | 84 | 145 | 101581.2 | 10 | 7005.6 | 108 | 75660.48 | 5 | 3502.8 | 88
[71 empty] | 2016-03-05 | [8 empty] | 0.45 | 322.758 |  |  |  | 2016-03-08 | 79.8138 | 14.1488 | 21991.6042 | 29150.1765 | 761.859 | 1654.3224 | 9722.772 | 9722.772 | [21 empty] | 2016-03-08 | 2016-03-08 | 87 | 87 | 173 | 125525.34 | 11 | 7981.38 | 119 | 86344.02 | 7 | 5079.06 | 96
[71 empty] | 2016-03-06 | [8 empty] | 0.46 | 329.9304 |  |  |  | 2016-03-09 | 30.6912 | 63.6842 | 22174.392 | 30311.3964 | 744.2616 | 2117.6928 | 7672.8 | 8056.44 | [21 empty] | 2016-03-09 | 2016-03-09 | 92 | 92 | 165 | 126601.2 | 7 | 5370.96 | 151 | 115859.28 | 4 | 3069.12 | 53
[71 empty] | 2016-03-07 | [8 empty] | 0.46 | 322.2576 |  |  |  | 2016-03-10 | 94.9509 | 0 | 20422.3248 | 28293.867 | 900.72 | 2026.62 | 6455.16 | 7430.94 | [21 empty] | 2016-03-10 | 2016-03-10 | 90 | 90 | 154 | 115592.4 | 8 | 6004.8 | 177 | 132856.2 | 6 | 4503.6 | 98
[71 empty] | 2016-03-08 | [8 empty] | 0.6 | 435.348 |  |  |  | 2016-03-11 | 80.7312 | 0 | 21912.6494 | 28384.356 | 1049.5056 | 1643.9808 | 6605.28 | 7559.376 | [21 empty] | 2016-03-11 | 2016-03-11 | 88 | 88 | 148 | 108620.16 | 8 | 5871.36 | 148 | 108620.16 | 7 | 5137.44 | 160
[71 empty] | 2016-03-09 | [8 empty] | 0.42 | 322.2576 |  |  |  | 2016-03-12 | 87.0696 | 14.1488 | 22228.1433 | 28116.225 | 1052.091 | 1255.2534 | 6530.22 | 7328.358 | [21 empty] | 2016-03-12 | 2016-03-12 | 87 | 87 | 162 | 117543.96 | 8 | 5804.64 | 139 | 100855.62 | 5 | 3627.9 | 48
[71 empty] | 2016-03-10 | [8 empty] | 0.41 | 307.746 |  |  |  | 2016-03-13 | 36.279 | 50.4278 | 22592.0217 | 30336.4998 | 921.4866 | 2205.7632 | 5732.082 | 6893.01 | [21 empty] | 2016-03-13 | 2016-03-13 | 87 | 87 | 181 | 131329.98 | 8 | 5804.64 | 155 | 112464.9 | 5 | 3627.9 | 104
[71 empty] | 2016-03-11 | [8 empty] | 0.45 | 330.264 |  |  |  | 2016-03-14 | 87.3365 | 448.5919 | 20412.3502 | 32626.4136 | 975.4464 | 2087.0016 | 9867.888 | 13610.88 | [21 empty] | 2016-03-14 | 2016-03-14 | 89 | 136 | 223 | 252935.52 | 24 | 27221.76 | 91 | 103215.84 | 11 | 12476.64 | 4000
[71 empty] | 2016-03-12 | [8 empty] | 0.45 | 326.511 |  |  |  | 2016-03-15 | 165.3322 | 22.0176 | 16632.4954 | 26469.1584 | 1112.8896 | 2033.6256 | 5604.48 | 7846.272 | [21 empty] | 2016-03-15 | 2016-03-15 | 96 | 96 | 158 | 126501.12 | 15 | 12009.6 | 123 | 98478.72 | 6 | 4803.84 | 156
[71 empty] | 2016-03-13 | [8 empty] | 0.44 | 319.2552 |  |  |  | 2016-03-16 | 70.2895 | 41.9585 | 19787.9344 | 26067.7292 | 1075.86 | 2230.6164 | 5737.92 | 6168.264 | [21 empty] | 2016-03-16 | 2016-03-16 | 86 | 86 | 150 | 107586 | 6 | 4303.44 | 135 | 96827.4 | 3 | 2151.72 | 30
[71 empty] | 2016-03-14 | [8 empty] | 0.51 | 578.4624 |  |  |  | 2016-03-17 | 14.5116 | 79.451 | 22163.2039 | 27680.877 | 812.6496 | 2154.9726 | 5586.966 | 6239.988 | [21 empty] | 2016-03-17 | 2016-03-17 | 87 | 87 | 173 | 125525.34 | 6 | 4353.48 | 143 | 103757.94 | 3 | 2176.74 | 34
[71 empty] | 2016-03-15 | 3.97 | 3178.5408 | 2.2195 | 1777.0205 | 6.45 | 5164.128 | 3.32 | 2658.1248 | 0.45 | 360.288 |  |  |  | 2016-03-18 | 14.0112 | 69.7057 | 20019.9031 | 27104.6664 | 868.6944 | 2374.8984 | 5394.312 | 5954.76 | [21 empty] | 2016-03-18 | 2016-03-18 | 84 | 84 | 137 | 95976.72 | 7 | 4903.92 | 144 | 100880.64 | 3 | 2101.68 | 38
[71 empty] | 2016-03-16 | [8 empty] | 0.46 | 329.9304 |  |  |  | 2016-03-19 | 0 | 79.451 | 22916.7187 | 29846.7333 | 798.138 | 2096.9262 | 5949.756 | 6385.104 | [21 empty] | 2016-03-19 | 2016-03-19 | 87 | 87 | 136 | 98678.88 | 6 | 4353.48 | 153 | 111013.74 | 4 | 2902.32 | 7
[71 empty] | 2016-03-17 | [8 empty] | 0.46 | 333.7668 |  |  |  | 2016-03-20 | 0 | 80.7479 | 24407.4187 | 30872.3448 | 854.5164 | 1920.702 | 7290.828 | 7917.996 | [21 empty] | 2016-03-20 | 2016-03-20 | 94 | 94 | 129 | 101130.84 | 8 | 6271.68 | 182 | 142680.72 | 4 | 3135.84 | 4
[71 empty] | 2016-03-18 | [8 empty] | 0.47 | 329.2632 |  |  |  | 2016-03-21 | 19.599 | 99.663 | 23301.126 | 31074.84 | 834 | 1542.9 | 7839.6 | 8340 | [21 empty] | 2016-03-21 | 2016-03-21 | 94 | 100 | 144 | 120096 | 10 | 8340 | 124 | 103416 | 6 | 5004 | 38
[71 empty] | 2016-03-19 | [8 empty] | 0.45 | 326.511 |  |  |  | 2016-03-22 | 2.7147 | 92.6866 | 24645.3255 | 31288.5108 | 1039.3308 | 1954.5624 | 5429.34 | 6515.208 | [21 empty] | 2016-03-22 | 2016-03-22 | 93 | 93 | 142 | 110138.04 | 9 | 6980.58 | 166 | 128752.92 | 5 | 3878.1 | 13
[71 empty] | 2016-03-20 | [8 empty] | 0.4 | 313.584 |  |  |  | 2016-03-23 | 0 | 82.2157 | 24843.8842 | 30318.9858 | 845.4258 | 1706.364 | 6282.522 | 6747.894 | [21 empty] | 2016-03-23 | 2016-03-23 | 93 | 93 | 163 | 126426.06 | 9 | 6980.58 | 162 | 125650.44 | 6 | 4653.72 | 37
[71 empty] | 2016-03-21 | [8 empty] | 0.46 | 383.64 |  |  |  | 2016-03-24 | 0 | 71.8074 | 22252.2376 | 27794.718 | 1001.8008 | 1856.484 | 4763.808 | 5254.2 | [21 empty] | 2016-03-24 | 2016-03-24 | 84 | 84 | 137 | 95976.72 | 8 | 5604.48 | 175 | 122598 | 5 | 3502.8 | 117
[71 empty] | 2016-03-22 | [8 empty] | 0.45 | 349.029 |  |  |  | 2016-03-25 | 0 | 60.9654 | 20967.1353 | 27987.372 | 808.146 | 1531.224 | 5742.09 | 6380.1 | [21 empty] | 2016-03-25 | 2016-03-25 | 84 | 85 | 155 | 109879.5 | 9 | 6380.1 | 154 | 109170.6 | 4 | 2835.6 | 40
[71 empty] | 2016-03-23 | [8 empty] | 0.5 | 387.81 |  |  |  | 2016-03-26 | 20.7666 | 50.5321 | 21892.8419 | 28083.3654 | 823.7418 | 1301.3736 | 6852.978 | 7060.644 | [21 empty] | 2016-03-26 | 2016-03-26 | 83 | 83 | 146 | 101064.12 | 9 | 6229.98 | 134 | 92757.48 | 4 | 2768.88 | 58
[71 empty] | 2016-03-24 | [8 empty] | 0.44 | 308.2464 |  |  |  | 2016-03-27 | 19.1403 | 37.5717 | 21946.8351 | 27682.545 | 723.078 | 1871.496 | 5387.64 | 5529.42 | [21 empty] | 2016-03-27 | 2016-03-27 | 85 | 85 | 140 | 99246 | 9 | 6380.1 | 158 | 112006.2 | 5 | 3544.5 | 63
[71 empty] | 2016-03-25 | [8 empty] | 0.44 | 311.916 |  |  |  | 2016-03-28 | 101.06 | 333.2247 | 19444.4806 | 29618.7594 | 1048.8384 | 2185.08 | 7538.526 | 10706.892 | [21 empty] | 2016-03-28 | 2016-03-28 | 85 | 131 | 175 | 191194.5 | 34 | 37146.36 | 71 | 77570.34 | 11 | 12017.94 | 4000
[71 empty] | 2016-03-26 | [8 empty] | 0.46 | 318.4212 |  |  |  | 2016-03-29 | 93.3496 | 51.9749 | 19187.2792 | 26900.4198 | 984.7872 | 2092.6728 | 3624.564 | 4445.22 | [21 empty] | 2016-03-29 | 2016-03-29 | 82 | 82 | 149 | 101898.12 | 7 | 4787.16 | 141 | 96427.08 | 3 | 2051.64 | 120
[71 empty] | 2016-03-27 | [8 empty] | 0.44 | 311.916 |  |  |  | 2016-03-30 | 104.1791 | 8.9989 | 20880.1241 | 27249.2403 | 1342.9068 | 2298.1704 | 3253.434 | 4222.542 | [21 empty] | 2016-03-30 | 2016-03-30 | 83 | 83 | 140 | 96910.8 | 6 | 4153.32 | 145 | 100371.9 | 2 | 1384.44 | 9
[71 empty] | 2016-03-28 | [8 empty] | 0.47 | 513.4938 |  |  |  | 2016-03-31 | 13.6776 | 56.4201 | 21107.6143 | 25836.9864 | 1032.6588 | 2414.0964 | 3761.34 | 4376.832 | [21 empty] | 2016-03-31 | 2016-03-31 | 82 | 82 | 124 | 84801.12 | 6 | 4103.28 | 150 | 102582 | 3 | 2051.64 | 18
[71 empty] | 2016-03-29 | [8 empty] | 0.43 | 294.0684 |  |  |  | Avg | 52.1378 | 81.1821 | 21379.4583 | 28412.3063 | 897.2091 | 1920.1881 | 6616.2834 | 7569.3302
[71 empty] | 2016-03-30 | [8 empty] | 0.43 | 297.6546
[71 empty] | 2016-03-31 | [8 empty] | 0.42 | 287.2296
[71 empty] | Monthly Avg. | 4.2572 | 3400 | 2.4272 | 1900 | 3.97 | 3200 | 2.295 | 1800 | 0.45806 | 300
[71 empty] | Daily Max | 4.5445 | 3600 | 2.635 | 2100 | 6.45 | 5200 | 3.32 | 2700 | 0.6 | 600

## NEW DMR
Bowery Bay | [6 empty] | 2016-03-01
Parameter | Type | Units | Sample Frequency | Sample Type | Influent | Effluent | Limitation | Value | Exceeds? (Yes/No)
PLANT DATA
Flow, Total | 12 month rolling average | MGD | Continuous | Recorder |  | X | 150 | 103 | No
Flow, Total | Monthly average | MGD | Continuous | Recorder |  | X | Monitor | 91 | N/A
Flow, Total | Daily Maximum | MGD | Continuous | Recorder |  | X | Monitor | 236 | N/A
Dissolved Oxygen | Daily Minimum conc. | mg/l | 1 / Day | Grab |  | X | Monitor | 2.47 | N/A
pH | Daily Minimum | SU | 6 / Day | Grab |  | X | 6 | 6.1 | No
pH | Daily Maximum | SU | 6 / Day | Grab |  | X | 9 | 7.4 | No
Temperature | Daily Maximum | Deg C | 6 / Day | Grab |  | X | Monitor | 19 | N/A
Chlorine, Total Residual | Daily Maximum conc. | mg/l | 6 / Day | Grab |  | X | 0.59 |  |  | see interim limit
Chlorine, Total Residual | Interim Limit from TRC C.O. | mg/l | 6 / Day | Grab |  | X | 1 | 0.6 | No
Chlorine, Total Residual | Daily Maximum load. | lbs/day | 6 / Day | Grab |  | X | Monitor | 600 | N/A
Chlorine, Total Residual | Monthly average conc. | mg/l | 6 / Day | Grab |  | X | Monitor | 0.45806 | N/A
Chlorine, Total Residual | Monthyly average load. | lbs/day | 6 / Day | Grab |  | X | Monitor | 300 | N/A
PROCESS LAB DATA
CBOD5 | Monthly average conc. | mg/l | 1 /Day | 24 hour Composite | X |  | Monitor | 144 | N/A
CBOD5 | Monthly average conc. | mg/l | 1 /Day | 24 hour Composite |  | X | 25 | 6 | No
CBOD5 | Monthly average load. | lbs/day | 1 /Day | 24 hour Composite | X |  | Monitor | 107600 | N/A
CBOD5 | Monthly average load. | lbs/day | 1 /Day | 24 hour Composite |  | X | 31000 | 4500 | No
CBOD5 | Monthly Percent Removal | % | 1 / month | calculated |  |  | 85 | 96 | No
CBOD5 | 7 day arithmetic mean conc. | mg/l | 1 /Day | 24 hour Composite | X |  | Monitor | 157 | N/A
CBOD5 | 7 day arithmetic mean conc. | mg/l | 1 /Day | 24 hour Composite |  | X | 40 | 8 | No
CBOD5 | 7 day arithmetic mean load. | lbs/day | 1 /Day | 24 hour Composite | X |  | Monitor | 118000 | N/A
CBOD5 | 7 day arithmetic mean load. | lbs/day | 1 /Day | 24 hour Composite |  | X | 50000 | 6100 | No
CBOD5 | Daily Maximum conc. | mg/l | 1 /Day | 24 hour Composite | X |  | Monitor | 182 | N/A
CBOD5 | Daily Maximum conc. | mg/l | 1 /Day | 24 hour Composite |  | X | Monitor | 21 | N/A
CBOD5 | Daily Maximum load. | lbs/day | 1 /Day | 24 hour Composite | X |  | Monitor | 142700 | N/A
CBOD5 | Daily Maximum load. | lbs/day | 1 /Day | 24 hour Composite |  | X | Monitor | 17200 | N/A
BOD5 | 6 consecutive hour avg. conc. | mg/l |  |  |  | X | 50 |  |  | IEC Limit
Solids, Suspended | Monthly average conc. | mg/l | 1 / Day | 24 hour Composite | X |  | Monitor | 149 | N/A
Solids, Suspended | Monthly average conc. | mg/l | 1 / Day | 24 hour Composite |  | X | 30 | 12 | No
Solids, Suspended | Monthly average load. | lbs/day | 1 / Day | 24 hour Composite | X |  | Monitor | 114600 | N/A
Solids, Suspended | Monthly average load. | lbs/day | 1 / Day | 24 hour Composite |  | X | 38000 | 9800 | No
Solids, Suspended | Monthly Percent Removal | % | 1 / month | calculated |  |  | 85 | 92 | No
Solids, Suspended | 7 day arithmetic mean conc. | mg/l | 1 / Day | 24 hour Composite | X |  | Monitor | 165 | N/A
Solids, Suspended | 7 day arithmetic mean conc. | mg/l | 1 / Day | 24 hour Composite |  | X | 45 | 20 | No
Solids, Suspended | 7 day arithmetic mean load. | lbs/day | 1 / Day | 24 hour Composite | X |  | Monitor | 134000 | N/A
Solids, Suspended | 7 day arithmetic mean load. | lbs/day | 1 / Day | 24 hour Composite |  | X | 56000 | 16000 | No
Solids, Suspended | Daily Maximum conc. | mg/l | 1 / Day | 24 hour Composite | X |  | Monitor | 223 | N/A
Solids, Suspended | Daily Maximum conc. | mg/l | 1 / Day | 24 hour Composite |  | X | 50 | 72 | Yes
Solids, Suspended | Daily Maximum load. | lbs/day | 1 /Day | 24 hour Composite | X |  | Monitor | 252900 | N/A
Solids, Suspended | Daily Maximum load. | lbs/day | 1 /Day | 24 hour Composite |  | X | Monitor | 58800 | N/A
Solids, Suspended | 6 consecutive hour avg. conc. | mg/l |  |  |  | X | 50 |  |  | IEC Limit
Phosphorus, Total (as P) | Monthly average conc. | mg/l | 2/month | 24 hour Composite | X |  | Monitor | 4.2572 | N/A
Phosphorus, Total (as P) | Monthly average conc. | mg/l | 2/month | 24 hour Composite |  | X | Monitor | 3.97 | N/A
Phosphorus, Total (as P) | Monthly average load. | lbs/day | 2/month | 24 hour Composite | X |  | Monitor | 3400 | N/A
Phosphorus, Total (as P) | Monthly average load. | lbs/day | 2/month | 24 hour Composite |  | X | Monitor | 3200 | N/A
Phosphorus, Total (as P) | Daily Maximum conc. | mg/l | 2/month | 24 hour Composite | X |  | Monitor | 4.5445 | N/A
Phosphorus, Total (as P) | Daily Maximum conc. | mg/l | 2/month | 24 hour Composite |  | X | Monitor | 6.45 | N/A
Phosphorus, Total (as P) | Daily Maximum load. | lbs/day | 2/month | 24 hour Composite | X |  | Monitor | 3600 | N/A
Phosphorus, Total (as P) | Daily Maximum load. | lbs/day | 2/month | 24 hour Composite |  | X | Monitor | 5200 | N/A
Soluble Orthophosphate (as P) | Monthly average conc. | mg/l | 2/month | 24 hour Composite | X |  | Monitor | 2.4272 | N/A
Soluble Orthophosphate (as P) | Monthly average conc. | mg/l | 2/month | 24 hour Composite |  | X | Monitor | 2.295 | N/A
Soluble Orthophosphate (as P) | Monthly average load. | lbs/day | 2/month | 24 hour Composite | X |  | Monitor | 1900 | N/A
Soluble Orthophosphate (as P) | Monthly average load. | lbs/day | 2/month | 24 hour Composite |  | X | Monitor | 1800 | N/A
Soluble Orthophosphate (as P) | Daily Maximum conc. | mg/l | 2/month | 24 hour Composite | X |  | Monitor | 2.635 | N/A
Soluble Orthophosphate (as P) | Daily Maximum conc. | mg/l | 2/month | 24 hour Composite |  | X | Monitor | 3.32 | N/A
Soluble Orthophosphate (as P) | Daily Maximum load. | lbs/day | 2/month | 24 hour Composite | X |  | Monitor | 2100 | N/A
Soluble Orthophosphate (as P) | Daily Maximum load. | lbs/day | 2/month | 24 hour Composite |  | X | Monitor | 2700 | N/A
Chlorides | Monthly average conc. | mg/l | 2/month | 24 hour Composite | X |  | Monitor | 400 | N/A
Chlorides | 12 month rolling average | mg/l | Continuous | 25 hour Composite | X |  | Monitor | 690
Nitrogen, TKN (as N) | ACTION LEVEL Annual Average load. | lbs/day | 1/year | 24 hour Composite | X |  | 32000 | 29400 | No | only report with December DMRs
Total Nitrogen from WWTP | 12 Month Rolling Average load. | lbs/day | 1/month | calculated |  | X | Monitor | 11300 | N/A
Total Nitrogen from WWTP | Monthly average conc. | mg/l | 1/day | 24 hour composite | X |  | Monitor | 37.9 | N/A
Total Nitrogen from WWTP | Monthly average conc. | mg/l | 1/day | 24 hour composite |  | X | Monitor | 13.6 | N/A
Total Nitrogen from WWTP | Monthly average load. | lbs/day | 1/day | 24 hour composite | X |  | Monitor | 28500 | N/A
Total Nitrogen from WWTP | Monthly average load. | lbs/day | 1/day | 24 hour composite |  | X | Monitor | 10400 | N/A
Nitrogen, Ammonia (as NH3) | Monthly average conc. | mg/l | 1/day | 24 hour composite | X |  | Monitor | 28.5 | N/A
Nitrogen, Ammonia (as NH3) | Monthly average conc. | mg/l | 1/day | 24 hour composite |  | X | 14 | 8.7 | No
Nitrogen, Ammonia (as NH3) | Monthly average load. | lbs/day | 1/day | 24 hour composite | X |  | Monitor | 21400 | N/A
Nitrogen, Ammonia (as NH3) | Monthly average load. | lbs/day | 1/day | 24 hour composite |  | X | Monitor | 6600 | N/A
Nitrogen, TKN (as N) | Monthly average conc. | mg/l | 1/day | 24 hour composite | X |  | Monitor | 37.7 | N/A
Nitrogen, TKN (as N) | Monthly average conc. | mg/l | 1/day | 24 hour composite |  | X | Monitor | 9.9 | N/A
Nitrogen, TKN (as N) | Monthly average load. | lbs/day | 1/day | 24 hour composite | X |  | Monitor | 28400 | N/A
Nitrogen, TKN (as N) | Monthly average load. | lbs/day | 1/day | 24 hour composite |  | X | Monitor | 7600 | N/A
Nitrate (NO3) as N | Monthly average conc. | mg/l | 1/day | 24 hour composite | X |  | Monitor | 0.1 | N/A
Nitrate (NO3) as N | Monthly average conc. | mg/l | 1/day | 24 hour composite |  | X | Monitor | 2.55 | N/A
Nitrate (NO3) as N | Monthly average load. | lbs/day | 1/day | 24 hour composite | X |  | Monitor | 100 | N/A
Nitrate (NO3) as N | Monthly average load. | lbs/day | 1/day | 24 hour composite |  | X | Monitor | 1900 | N/A
Nitrite (NO2) as N | Monthly average conc. | mg/l | 1/day | 24 hour composite | X |  | Monitor | 0.07 | N/A
Nitrite (NO2) as N | Monthly average conc. | mg/l | 1/day | 24 hour composite |  | X | Monitor | 1.19 | N/A
Nitrite (NO2) as N | Monthly average load. | lbs/day | 1/day | 24 hour composite | X |  | Monitor | 100 | N/A
Nitrite (NO2) as N | Monthly average load. | lbs/day | 1/day | 24 hour composite |  | X | Monitor | 900 | N/A
MICROBIOLOGY LAB DATA
Coliform, Fecal | 30 day geometric mean | No./100 ml | 1 / Day | Grab |  | X | 200 | 67 | No
Coliform, Fecal | 7 day geometric mean | No./100 ml | 1 / Day | Grab |  | X | 400 | 91 | No
Coliform, Fecal | 6 hour geometric mean | No./100 ml |  |  |  | X | 800 |  |  | IEC Limit
Coliform, Fecal | Instantaneous Maximum | No./100 ml |  |  |  | X | 2400 |  |  | IEC Limit
Enterococcus | Daily Maximum | No./100 ml | 1/month | Grab |  | X | Monitor | 100 | N/A

## DMR
NYCDEP - PROCESS ENGINEERING SECTION
DISCHARGE MONITORING REPORT
Bowery Bay | MONTH: | 2016-03-01 |  | 2016 |  |  |  | Limits
PARAMETER | VALUES |  |  |  | # OF VIOL. |  |  | Plant Specific Limits
Temperature, Celsius | Avg Month | 18 | Max: | 19
Dissolved Oxygen, Effluent | Minimum | 2.47 | Avg: | 4.1
CBOD Influent, 30-Day Concentration | Avg Month | 144
CBOD Effluent, 30-Day Conc & Loading | Avg Month | 6 | Load: | 4500 | 0 | / | 0 | 25 | 31000
CBOD Effluent, 7-Day Conc & Loading | Max. Week | 8 | Load: | 6100 | 0 | / | 0 | 40 | 50000
TSS Influent, 30-Day Concentration | Avg Month | 149
TSS Effluent, 30-Day Conc & Loading | Avg Month | 12 | Load: | 9800 | 0 | / | 0 | 30 | 38000
TSS Effluent 7-Day Conc & Loading | Max. Week | 20 | Load: | 16000 | 0 | / | 0 | 45 | 56000
TSS Effluent, Daily | Daily Max | 72 |  |  |  | 1 |  | 50 |  | For violation on Day 1, check the flow
pH Influent | Min | 6.3 | Max: | 7.7 | [5 empty] | for the last day of previous month.
pH Effluent | Min | 6.1 | Max: | 7.4 | 0 | / | 0 | 6 | 9
Settleable Solids, Influent | Daily Max Avg
Settleable Solids, Effluent | Daily Max Avg
Flow (Plant/Dry Weather) | Avg Month | 91 | Dry: | 87
Daily Flow 12-Month Rolling Average |  | 103 |  |  |  | 0 |  | 150
CBOD Percent Removal | 96% |  |  |  |  | 0 |  | 85%
TSS Percent Removal | 92% |  |  |  |  | 0 |  | 85%
Max Daily Chlorine Residual | 0.6 | mg/L |  |  |  | 0 |  | 2
Max Daily Fecal Coliform | 4000 | #/100 ml
30 - Day Geometric Fecal Coliform | 67 | #/100 ml |  |  |  | 0 |  | 200
7 - Day Max Geometric Fecal Average | 91 | #/100 ml |  |  |  | 0 |  | 400
Chlorides (mg/L) | Avg Month | 400 | Max: | 1400
Maximum Hourly Flow | 236 | MGD
Current Wet Weather Capacity | 300 | MGD | REMARK
Total Influent Nitrogen Monthly Average Conc. & Loading | Avg Month: | 37.9 | Load: | 28500
Total Effluent Nitrogen Monthly Average Conc. & Loading | Avg Month: | 13.6 | Load: | 10400
Total Effluent Nitrogen 12-Month Rolling Average (lbs/day): |  | 11300
NO2 Influent, 30-Day Conc & Loading | Avg Month: | 0.07 | Load: | 100
NO2 Effluent, 30-Day Conc & Loading | Avg Month: | 1.19 | Load: | 900
NO3 Influent, 30-Day Conc & Loading | Avg Month: | 0.1 | Load: | 100
NO3 Effluent, 30-Day Conc & Loading | Avg Month: | 2.55 | Load: | 1900
TKN Influent, 30-Day Conc & Loading | Avg Month: | 37.7 | Load: | 28400
TKN Effluent, 30-Day Conc & Loading | Avg Month: | 9.9 | Load: | 7600
NH3 Influent, 30-Day Conc & Loading | Avg Month: | 28.5 | Load: | 21400
NH3 Effluent, 30-Day Conc & Loading | Avg Month: | 8.7 | Load: | 6600
Orthophosphate (mg/L) | Influent | 2.4 | Effluent | 2.3
Total Phosphorous (mg/L) | Influent | 4.3 | Effluent | 4
All averages are arithmetic means.
REMARKS: | Note:-
(1) Plant did not throttle during the month. | Contact tank flows were used during the month.
(2) Restricted flow caused by mechanical problems.
(3) Restricted flow due to construction activities.
(4) Sanitary system.
(5) Other.
PROCESS ENGINEER:
PLANT CHIEF:

## dmr NC
Non-Compliance | [6 empty] | Cause (A) mechanical failure | Possible Corrective Action (1) in-house repairs
MONITORING PERIOD: |  |  |  | PLANT: | Bowery Bay |  | (B) electrical failure (C) biological upset (D) non-rep. sample | (2) contractual repairs (3) purchase parts (4) under investigation
From: | 3 | 1 | 2016 |  |  |  | (E) sample error (F) lab instrument failure (G) process unit failure | (5) additional training (6) process correction (7) additional testing
To: | 3 | 31 | 2016 | SPDES Permit Number: |  | NY-0026158 | (H) illegal discharge (I) more investigation required | (8) notified IPP (9) no action required (10) under construction
| Month | Day | Year |  |  |  | (J) late notification (K) human error (L) combined sewer | page 2
Date(s) of Non-Compliance |  | Type of Failure |  | Quantity | Remarks
|  | Effluent: high pH |  | 0
|  | Effluent: low pH |  | 0
|  | Chlorine Residual |  | 0
|  | SS Effluent 7-day |  | 0
|  | SS 7 day loading |  | 0
|  | SS Effluent 30-day |  | 0
|  | SS 30 day loading |  | 0
|  | < % removal SS |  | 0
2016-03-02 |  | Daily Effluent TSS conc. |  | 1 | On March 2, 2016 Bowery Bay exceeded the limit for the daily effluent total suspended solids concentration of 50 mg/L with effluent values of 72 mg/L. The excursion on March 2, 2016 is attributed to high influent flow due to prolong wet weather event and influent flow distribution limitations directly related to the Forcemain leakage and associated pumping scheme. The North Battery was hydraulic overloaded which caused the solids washout.
|  | BOD Effluent 7-day |  | 0
|  | BOD 7 day loading |  | 0
|  | BOD Effluent 30-day |  | 0
|  | BOD 30 day loading |  | 0
|  | < % removal BOD |  | 0
|  | Fecal 30-day |  | 0
|  | Fecal 7-day |  | 0
|  | Excessive Flow |  | 0
|  | Sampling Anomaly |  | 0

## AT_
|  | 104.272 |  | 99.2561 |  |  |  | 41.7704 | 55.2973 | -12.7639
|  | 191.728 |  | 196.7439 |  |  |  | 110.2296 | 114.7027 | 36.7639
|  | Bowery Bay WPCP Analytical and Treatment Sheet | [16 empty] | 2016-03-01 |  | 2016 |  |  |  |  | Bowery Bay WPCP Analytical and Treatment Sheet | [13 empty] | 2016-03-01 |  | 2016 | [5 empty] | Bowery Bay WPCP Analytical and Treatment Sheet | [27 empty] | 2016-03-01 |  | 2016 |  |  |  |  | Bowery Bay WPCP Analytical and Treatment Sheet | [17 empty] | 2016-03-01 |  | 2016 |  |  |  |  | Bowery Bay WPCP Analytical and Treatment Sheet | [14 empty] | 2016-03-01 |  | 2016 |  |  |  | Bowery Bay WPCP Analytical and Treatment Sheet | [9 empty] | 2016-03-01 |  | 2016 |  |  |  |  | Bowery Bay WPCP Nutrient Sheet | [30 empty] | 2016-03-01 |  | 2016 |  |  |  | Bowery Bay WPCP Nutrient Sheet | [18 empty] | 2016-03-01 |  | 2016
FACTORS
|  | Suspended Solids (mg/L) | [17 empty] | Sludge | [5 empty] | Carb. Biochemical Oxygen Demand (mg/L) | [5 empty] | Thickener | Thickened |  | Primary |  | Volatile Dest. |  | Cylinders (30 min) |  | F/M |  | SRT |  |  |  | Digester Control | [14 empty] | Aerator Effluent |  |  |  | Plant | Chlorides |  |  | Plant | pH | [5 empty] | Sample | [9 empty] | Return Sludge |  | Air |  | Detention Time (hours) |  |  | Surface |  |  | Suspended Solids |  |  |  |  | Sludge Age (days) |  |  |  |  | Rakings | Grit |  | Scum |  | Thickened Sludge |  |  | Digested Sludge |  |  | Bowery Bay Sludge |  |  |  | Average | Sodium |  |  |  |  | Power |  |  |  | Digester gas (x 1000 cuft) |  |  |  | Fuel Oil (gallons) |  |  | Natural Gas (x1000 cuft) | [5 empty] | Influent (mg/L) | [20 empty] | Primary Effluent (mg/L) | [6 empty] | Plant Effluent (mg/L) | [33 empty] | TANKS IN SERVICE | [8 empty] | Return Sludge MGD |  |  | 0.00417 | CONVERSION OF mg/l TO Tons/Gallon |  | SCT
| D | Raw Sewage | [5 empty] | Prim Eff |  | Plant | Thick | Aerator Effluent |  | Average Aerator |  | Return Sludge |  |  |  | Density |  |  |  | D | D | Raw |  |  | Primary |  | Plant | influent | Sludge |  | Digester |  |  |  | South | North |  |  |  |  | D | D | Digester Volatiles |  |  |  |  | Alkalinity |  |  |  |  | pH |  |  |  |  | Dissolved Oxygen (mg/L) |  |  |  | Eff | Influent (mg/L) |  |  | Eff | Plant |  |  | Plant |  |  | Chlorine | Fecal |  | D | D | Plant Flows (MGD) | [5 empty] | % |  | Cu. Ft. |  |  |  | Loading | Sludge | Aeration | Load | % | Dry | Tons | Pri Eff |  |  |  | D | D |  |  | Dry |  | Dry |  |  |  | To Storage |  |  | To Centrifuges |  |  |  | Digester | Hypochlorite |  |  | D | D | X 1000 KWH |  |  |  |  | To Boilers | Vented | Flared |  | To Boilers | To |  | To Boilers |  | Weather | D | D | High Level | [6 empty] | Lower Level | [6 empty] | Plant Influent | [20 empty] | D | D | RAW CENTRATE | [7 empty] | Treated Centrate Tank | [14 empty] | D | D | PRIMARY | AER. | AER. | F-1,4,8,11 | F-2,3,9,10 | F-5,7 | F-6 | F-12,14,15,17 | F-13,16 |  |  |  | 64 | GRIT FACTOR
| A | High Level |  | Lower Level |  | Plant |  | South | North | Eff | Eff | South | North | South | North | South |  | North |  | Index |  |  |  | A | A | Sewage |  | Plant | Effluent |  |  | SS |  |  | Sludge |  |  |  | (ml/L) | (ml/L) | South | North | South | North | A | A | (mg/L) |  |  |  |  | (mg/L) | [9 empty] | South |  | North |  | D.O. | High | Lower | Plant | Temp | Influent |  |  | Effluent |  |  | Resid. | Coliform |  | A | A | [5 empty] | MGD | Plant | MCF | Per | Primary | Aeration | Final | Rate | Density | Tanks | Dry | Removal | Tons | Under | Tons | South | North | Plant | A | A | Cu. Ft. | Cu. Ft. | Lbs | Cu. Ft. | Lbs | Cu. Ft. | Dry Lbs | Lbs Vol | Cu. Ft. | Dry Lbs | Lbs Vol | Cu. Ft. | Dry Lbs | Dry | Foreign | Temp | gals |  | Average | A | A | Gener | Purchase | Total | To | Produced | Main |  |  | Total | Main | Generators | Total | Main | Dewatering |  | A | A | Nitrogen |  |  |  | Phosphorus |  | Demand | Nitrogen |  |  |  | Phosphorus |  | Demand | Nitrogen |  |  |  | Phosphorus |  | Demand | Nitrogen |  |  |  | Phosphorous |  | Demand | Nitrogen |  |  |  | Phosphorous |  | Demand | A | A | pH | Nitrogen |  | Phosphorus | SS | VOL. SS | CBOD | ALK | NO2 |  | NO3 |  | NH3 |  | Alkalinity |  | pH |  | TSS (mg/L) |  |  |  |  | A | A | 0.54 | 2.52 | 2.52 | 0.954 | 0.915 | 1.234 | 1.159 | 1.155 | 1.095 | South | North |  | 27 | SCUM FACTOR
| Y | Total | % Vol | Total | % Vol | Total | % Vol | (mg/L) | (mg/L) | (mg/L) | (mg/L) | (mg/L) | (mg/L) | (mg/L) | (mg/L) | (mg/L) | %VOL. | (mg/L) | %VOL. | South | North |  |  | Y | Y | H.L. | L.L. | Total | South | North | Effluent | mg/L | % SOL | % VOL | %SOL | %VOL | % |  |  |  | /d | /d | Day | Day | Y | Y | No. 3 | No. 5 | No. 6 | No.7 | No.8 | No. 3 | No. 5 | No. 6 | No.7 | No.8 | No. 3 | No. 5 | No. 6 | No.7 | No.8 | A.M. | P.M. | A.M. | P.M. | (mg/L) | Level | Level | Influent | °C | Max | Min | Avg | Max | Min | Avg | mg/L | 100ml |  | Y | Y | Daily | Dry | Max | Min | Aer |  | Flow |  | gal | Tanks | Tanks | Tanks | gpd/sq ft | Index | Operation | Tons |  | Removed | Air | Load |  |  |  | Y | Y | [5 empty] | x1000 | x1000 | x1000 | x1000 | x1000 | x1000 | x1000 | x1000 | Tons | Sludge | °F | Total | / MG | Residual | Y | Y |  |  |  | Blowers |  | building |  |  |  | building |  |  | building | building |  | Y | Y | NO2 | NO3 | NH3 | TKN | Ortho | Total | COD | NO2 | NO3 | NH3 | TKN | Ortho | Total | COD | NO2 | NO3 | NH3 | TKN | Ortho | Total | COD | NO2 | NO3 | NH3 | TKN | Ortho | Total | COD | NO2 | NO3 | NH3 | TKN | Ortho | Total | COD | Y | Y |  | NH3 | Alk | Total | (mg/L) | % | (mg/L) | (mg/L) | Inf | Eff | Inf | Eff | Inf | Eff | Inf | Eff | Inf | Eff | Inf | Eff |  |  |  | Y | Y |  | SOUTH | NORTH | 0.01055 | 0.012125 | 0.013655 | 0.012825 | 0.012775 | 0.01211 |  |  |  | 63 | SLUDGE FACTOR |  | pH
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 |  |  |  |  | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 |  |  | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 |  | 71 |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 |  |  | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 |  |  | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 |  |  | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 52 | 53 | [5 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 1 | 2 |  | 50 | RAKINGS FACTOR (#/CU FT)
| 1 | 119 |  | 120 |  | 119 |  | 50 | 72 | 7 | 160 | 5000 | 3300 | 4800 | 4700 | 7680 |  | 5080 |  | 1.7857 | 1.0645 |  |  | 1 | 1 | 138 | 162 | 146 | 90 | 89 | 5 | 2060 | 3.8 | 79.7 | 2.1 | 69.2 | 52% |  | 280 | 310 | 0.077712 | 0.078483 | 5.3391 | 15.0* | 1 | 1 | [15 empty] | 3.98 | 4.1 | 4.08 | 4.36 | 4.1 | 96 | 155 | 120 | 17 | 7 | 6.7 | 6.9 | 7.4 | 6.4 | 6.7 | 0.36 |  | 128 | 1 | 1 | 94 | 86 | 156 | 60 | 94 | 50 | 53.19% | 93.8 | 0.99787 | 1.9 | 3.8 | 3.7 | 550 | 1.4 |  | 46.6 | 94.206 | 43.9 | 450.8 | 23 | 23.2* | 15.8* | 19.6 | 1 | 1 | 162 | 0 | 0 |  |  | 72 | 172.4 | 137.4 | 72 | 95.3 | 65.9 |  |  |  |  | 103 | 690 | 7.3 | 0.44 | 1 | 1 |  | 134.4 | 134.4 | 53.8042 |  |  | 227.9 | 683.7 | [6 empty] | Rain | 1 | 1 | 0.04 | 0.16 | 27.56 | 37.4 | 2.67 | 4.59 | 373 | 0.04 | 0.12 | 27.7 | 37.4 | 2.57 | 4.46 | 363 | 0.04 | 0.146 | 27.609 | 37.4 | 2.635 | 4.5445 | 369.5 | 0 | 0.02 | 22.5 | 31.3 | 2.56 | 4.72 | 233 | 0.83 | 2.8 | 11.8 | 12.1 | 1.27 | 1.49 | 47 | 1 | 1 | [23 empty] | 1 | 1 | 14 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 87 | 85 | 122 | 80 | GRIT FACTOR (#/CU FT)
| 2 | 136 | 78 | 112 | 80.4 | 128 | 78.8 | 84 | 72 | 72 | 176 | 2100 | 2100 | 3700 | 3500 | 7520 | 80.3 | 7860 | 78.4 | 1.1667 | 0.75 |  |  | 2 | 2 | 140 | 133 | 138 | 68 | 63 | 21 | 2240 | 3.4 | 81.2 | 2.5 | 71 | 36% |  | 180 | 280 | 0.079413 | 0.077778 | 3.1814 | 4.2823 | 2 | 2 | [15 empty] | 4.25 | 4.57 | 4.21 | 5.46 | 3.76 |  |  |  | 17 | 7.2 | 6.6 | 6.9 | 6.6 | 6.4 | 6.5 | 0.69 |  | 92 | 2 | 2 | 98 | 85 | 171 | 47 | 98 | 55 | 56.12% | 99.6 | 1.0163 | 1.9 | 3.6 | 3.6 | 580 | 1 | S | 52.3 | 43.7859 | 22.9 | 343.6 | 32.4 | 10.2 | 11.3 | 10.6 | 2 | 2 | 162 | 0 | 0 |  |  | 65.7 | 140.7 | 114.2 | 65.7 | 103.5 | 73.5 |  |  |  |  | 103 | 1650 | 16.8 | 0.43 | 2 | 2 |  | 131.2 | 131.2 | 57.204 | N | See | 227.9 | 683.7 | [6 empty] | Rain | 2 | 2 | 1: 0.12; 2: 0.24; 3: 21.86; 4: 31.7; 8: 0.11; 9: 0.24; 10: 22.7; 11: 31; 15: 0.1165; 16: 0.24; 17: 22.154; 18: 31.455; 29: 0.86; 30: 2.73; 31: 11.3; 32: 16.2 | 2 | 2 | [23 empty] | 2 | 2 | 14 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 18 | 17 | -20 | 60 | SCUM FACTOR (#/CU FT)
| 3 | 124 |  | 151 |  | 133 |  | 54 | 100 | 20 | 96 | 2700 | 3100 | 5100 | 3900 | 5500 |  | 4650 |  | 1.08 | 0.64583 |  |  | 3 | 3 | 171 | 191 | 178 | 98 | 132 | 8 | 940 | 3.46 | 82 | 2 | 68 | 52% |  | 250 | 480 | 0.069475 | 0.12237 | 7.3342 | 10.5568 | 3 | 3 | 190 |  | 140 | 450 | 180 | 3500 |  | 3800 | 3200 | 3000 | 7.1 |  | 7.2 | 6.9 | 7.1 | 4.05 | 3.44 | 5.09 | 4 | 4.64 |  |  |  | 17 | 7.4 | 6.6 | 6.9 | 6.5 | 6.3 | 6.4 | 0.36 |  | 109 | 3 | 3 | 82 | 82 | 97 | 48 | 82 | 59 | 71.95% | 101.4 | 1.2366 | 2.2 | 3.9 | 4.3 | 480 | 0.9 |  | 45.5 | 85.0549 | 38.7 | 444.5 | 24.8 | 26.1* | 10.8 | 17.9 | 3 | 3 |  | 324 | 20700 |  |  | 63.1 | 137.5 | 112.8 | 63.1 | 79.5 | 54.1 |  |  |  |  | 104 | 1070 | 13 | 0.6 | 3 | 3 |  | 134.4 | 134.4 | 57.4361 | O | Notes | 227.9 | 683.7 | [6 empty] | Clear | 3 | 3 | 1: 0.13; 2: 0.14; 3: 28.9; 4: 38.7; 8: 0.11; 9: 0.1; 10: 28.3; 11: 38.3; 15: 0.123; 16: 0.126; 17: 28.69; 18: 38.56; 29: 1.06; 30: 3.09; 31: 10.8; 32: 11.7 | 3 | 3 | [23 empty] | 3 | 3 | 14 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 39 | 79 | 59
| 4 | 120 |  | 130 |  | 124 |  |  |  | 9 | [13 empty] | 4 | 4 | 124 | 111 | 119 |  |  | 4 | [7 empty] | 300 | 790 | 0.08768 | 0.086672 | 5.1953 | 9.1427 | 4 | 4 | [15 empty] | 3.96 | 3.63 | 4.52 | 4.52 | 4.06 |  |  |  | 17 | 7.3 | 6.6 | 7 | 6.9 | 6.3 | 6.6 | 0.39 |  | 56 | 4 | 4 | 96 | 90 | 146 | 43 | 96 | 59 | 61.46% | 101.2 | 1.0542 | 1.9 | 3.5 | 3.7 | 570 |  | T | 49.6 | 92.7419 | 46 | 397.2 | 31.9 | 13.1 | 11.7 | 12.5 | 4 | 4 |  | 324 | 20700 |  |  | 49.9 | 106.9 | 87.8 | 49.9 | 59.7 | 41.3 |  |  |  |  | 104 | 830 | 8.6 | 0.45 | 4 | 4 |  | 134.4 | 134.4 | 56.316 |  | Below | 227.9 | 683.7 | [6 empty] | Snow | 4 | 4 | 1: 0.11; 2: 0.12; 3: 27.81; 4: 35.5; 8: 0.1; 9: 0.11; 10: 26.7; 11: 35.8; 15: 0.1065; 16: 0.1165; 17: 27.4215; 18: 35.605; 29: 1.03; 30: 2.48; 31: 10.7; 32: 11.3 | 4 | 4 | [23 empty] | 4 | 4 | 14 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 37 | 58 | 36 | 1.7129 | Secondary Sludge Wasting South: MGD
| 5 | 142 |  | 106 |  | 129 |  |  |  | 9 | [13 empty] | 5 | 5 | 165 | 154 | 161 |  |  | 6 | [7 empty] | 320 | 420 | 0.078546 | 0.077643 | 5.2209 | 10.5385 | 5 | 5 | [15 empty] | 4.27 | 3.56 | 6.14 | 5.89 | 4.68 |  |  |  | 17 | 7.5 | 6.7 | 7 | 6.8 | 6.6 | 6.7 | 0.49 |  | 73 | 5 | 5 | 86 | 86 | 108 | 42 | 86 | 59 | 68.6% | 99.2 | 1.1535 | 2.3 | 3.8 | 4.1 | 510 |  |  | 46.3 | 93.0886 | 43.1 | 397.2 | 28.5 | 14.6 | 13 | 13.9 | 5 | 5 | 162 | 0 | 0 |  |  | 49.2 | 105.4 | 86.5 | 49.2 | 58.9 | 40.7 |  |  |  |  | 104 | 1020 | 11.9 | 0.45 | 5 | 5 |  | 150.4 | 150.4 | 56.328 | M |  | 227.9 | 683.7 | [6 empty] | Clear | 5 | 5 | 1: 0.05; 2: 0.07; 3: 30.96; 4: 39.4; 8: 0.06; 9: 0.07; 10: 30.7; 11: 38; 15: 0.0535; 16: 0.07; 17: 30.869; 18: 38.91; 29: 1.2; 30: 2.68; 31: 9.7; 32: 10.6 | 5 | 5 | [23 empty] | 5 | 5 | 15 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 33 | 52 | 26 | 0.57877 | Secondary Sludge Wasting North: MGD
| 6 | 142 |  | 136 |  | 140 |  | 64 | 79 | 10 |  | 2400 | 2800 | 3500 | 6500 | 5840 |  | 4740 |  | 0.68571 | 0.6087 |  |  | 6 | 6 | 160 | 160 | 160 |  |  | 6 | [7 empty] | 350 | 460 | 0.094255 | 0.05017 | 5.0036 | 19.9* | 6 | 6 | [15 empty] | 3.67 | 3.85 | 4.35 | 5.06 | 4.31 |  |  |  | 17 | 7.5 | 6.7 | 6.9 | 7.1 | 6.4 | 6.8 | 0.43 |  | 144 | 6 | 6 | 86 | 86 | 108 | 44 | 86 | 59 | 68.6% | 100.2 | 1.1651 | 2.3 | 3.8 | 4.1 | 510 | 0.6 | E | 50.2 | 92.8287 | 46.6 | 425.6 | 25.1 | 23.9* | 21.7* | 17 | 6 | 6 |  | 162 | 10400 |  |  | 64.7 | 138.6 | 113.8 | 64.7 | 77.4 | 53.5 |  |  |  |  | 105 | 880 | 10.2 | 0.46 | 6 | 6 |  | 140.8 | 140.8 | 56.124 | E |  | 227.9 | 683.7 | [6 empty] | Clear | 6 | 6 | 1: 0.05; 2: 0.12; 3: 30.84; 4: 39.8; 8: 0.09; 9: 0.04; 10: 30.6; 11: 38; 15: 0.064; 16: 0.092; 17: 30.756; 18: 39.17; 29: 1.11; 30: 2.08; 31: 9.6; 32: 11.1 | 6 | 6 | [23 empty] | 6 | 6 | 15 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 29 | 60 | 30
| 7 | 146 | 78.1 | 142 | 77.5 | 145 | 77.9 | 66 | 76 | 10 | 150 | 2500 | 2800 | 4000 | 3700 | 5860 | 80.9 | 5080 | 79.9 | 1.3158 | 0.63636 |  |  | 7 | 7 | 107 | 111 | 108 | 81 | 82 | 5 | 640 | 3.23 | 83.5 | 1.81 | 67.4 | 55% |  | 190 | 440 | 0.075 | 0.082082 | 5.7071 | 10.4321 | 7 | 7 | 170 |  | 180 | 130 | 130 | 3600 |  | 3800 | 2000 | 3800 | 7.29 |  | 7.36 | 7.12 | 7.2 | 3.49 | 3.6 | 4.25 | 4.37 | 3.75 |  |  |  | 17 | 7.2 | 6.6 | 6.9 | 6.8 | 6.5 | 6.6 | 0.33 |  | 88 | 7 | 7 | 84 | 84 | 110 | 32 | 84 | 59 | 70.24% | 101.1 | 1.2036 | 2.3 | 3.8 | 4.2 | 490 | 1 |  | 50.8 | 93.1102 | 47.3 | 368.8 | 24.5 | 16.4* | 13.1 | 15.1 | 7 | 7 |  | 324 | 20700 |  |  | 48.7 | 99.1 | 82.7 | 48.7 | 55.5 | 37.4 |  |  |  |  | 105 | 1170 | 13.9 | 0.46 | 7 | 7 |  | 124.8 | 124.8 | 56.3801 | T |  | 227.9 | 683.7 | [6 empty] | Clear | 7 | 7 | 1: 0.14; 2: 0; 3: 27.69; 4: 36.9; 8: 0.15; 9: 0; 10: 26.5; 11: 36.6; 15: 0.1435; 16: 0; 17: 27.2735; 18: 36.795; 29: 1.2; 30: 1.47; 31: 11.7; 32: 12.3 | 7 | 7 | [23 empty] | 7 | 7 | 15 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 30 | 50 | 21
| 8 | 176 |  | 168 |  | 173 |  | 96 | 78 | 11 | 160 | 3500 | 2200 | 3600 | 3900 | 8060 |  | 5500 |  | 1.5909 | 0.6875 |  |  | 8 | 8 | 106 | 142 | 119 | 106 | 77 | 7 | 960 | 4.16 | 85.6 | 1.92 | 68 | 63% |  | 220 | 320 | 0.11295 | 0.075736 | 3.7686 | 10.1431 | 8 | 8 | [15 empty] | 3.21 | 3.89 | 3.34 | 3.93 | 3.69 | 137 | 337 | 210 | 17 | 7.4 | 6.6 | 6.9 | 6.8 | 6.6 | 6.7 | 0.22 |  | 96 | 8 | 8 | 87 | 87 | 100 | 53 | 87 | 59 | 67.82% | 98.1 | 1.1276 | 2.2 | 3.7 | 4 | 510 | 1.1 | P | 62.8 | 93.6306 | 58.8 | 349.9 | 32.2 | 9.8 | 13 | 10.9 | 8 | 8 |  | 972 | 62200 |  |  | 70.1 | 183.7 | 157.2 | 70.1 | 84.8 | 57.7 |  |  |  |  | 106 | 970 | 11.1 | 0.6 | 8 | 8 |  | 131.2 | 131.2 | 56.4158 | E |  | 227.9 | 683.7 | [6 empty] | Clear | 8 | 8 | 1: 0.11; 2: 0.03; 3: 30.96; 4: 41.4; 8: 0.11; 9: 0; 10: 29.1; 11: 37.9; 15: 0.11; 16: 0.0195; 17: 30.309; 18: 40.175; 22: 0.07; 23: 0; 24: 25.7; 29: 1.05; 30: 2.28; 31: 13.4; 32: 13.4 | 8 | 8 | [23 empty] | 8 | 8 | 15 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 32 | 28 | 1
| 9 | 164 | 82.9 | 168 | 81 | 165 | 82.2 | 84 | 70 | 7 | 210 | 2500 | 3200 | 4400 | 4600 | 6500 | 78.2 | 6660 | 77.5 | 1.4706 | 0.66667 |  |  | 9 | 9 | 148 | 157 | 151 | 81 | 82 | 4 | 1760 | 3.5 | 83.3 | 2 | 68.5 | 53% |  | 170 | 480 | 0.074675 | 0.07231 | 5.7536 | 10.4358 | 9 | 9 | [15 empty] | 3.99 | 4.02 | 4.48 | 4.78 | 4.42 |  |  |  | 18 | 7.5 | 6.5 | 6.9 | 6.6 | 6.4 | 6.5 | 0.54 |  | 53 | 9 | 9 | 92 | 92 | 112 | 54 | 92 | 59 | 64.13% | 98.1 | 1.0663 | 2 | 3.6 | 3.8 | 540 | 1.1 |  | 63.3 | 95.7346 | 60.6 | 422.4 | 30.1 | 12.9 | 16.2* | 14 | 9 | 9 |  | 0 | 0 |  |  | 72.4 | 159.6 | 132.9 | 72.4 | 91.2 | 62.5 |  |  |  |  | 107 | 690 | 7.5 | 0.42 | 9 | 9 |  | 131.2 | 131.2 | 54.372 | R |  | 227.9 | 683.7 | [6 empty] | Clear | 9 | 9 | 1: 0.04; 2: 0.09; 3: 28.9; 4: 39.4; 8: 0.04; 9: 0.07; 10: 28.9; 11: 39.7; 15: 0.04; 16: 0.083; 17: 28.9; 18: 39.505; 29: 0.97; 30: 2.76; 31: 10; 32: 10.5 | 9 | 9 | [23 empty] | 9 | 9 | 14 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 28 | 42 | 11 |  |  |  | 9.06
| 10 | 152 |  | 158 |  | 154 |  | 66 | 106 | 8 | 120 | 3100 | 3500 | 5200 | 4900 | 6400 |  | 6400 |  | 1.069 | 0.83333 |  |  | 10 | 10 | 175 | 181 | 177 | 97 | 108 | 6 | 1980 | 3.4 | 81.4 | 1.99 | 68 | 51% |  | 290 | 420 | 0.074023 | 0.087464 | 6.8714 | 10.5435 | 10 | 10 | 220 |  | 200 | 190 | 160 | 3100 |  | 3200 | 3100 | 3100 | 7.1 |  | 7.1 | 7.1 | 7.1 | 3.73 | 4.2 | 3.75 | 4.37 | 3.56 |  |  |  | 18 | 7.2 | 6.6 | 6.8 | 6.7 | 6.5 | 6.6 | 0.38 |  | 98 | 10 | 10 | 90 | 90 | 111 | 64 | 90 | 59 | 65.56% | 95.6 | 1.0622 | 2 | 3.7 | 3.9 | 530 | 1 |  | 57.8 | 94.8097 | 54.8 | 482.3 | 30.8 | 19.9* | 11.6 | 15.7 | 10 | 10 |  | 324 | 20700 |  |  | 66.8 | 143.1 | 116.5 | 66.8 | 83.7 | 56.9 |  |  |  |  | 108 | 930 | 10.3 | 0.41 | 10 | 10 |  | 131.2 | 131.2 | 55.6121 |  |  | 227.9 | 683.7 | [6 empty] | Clear | 10 | 10 | 1: 0.13; 2: 0; 3: 27.32; 4: 37.8; 8: 0.12; 9: 0; 10: 27; 11: 37.5; 15: 0.1265; 16: 0; 17: 27.208; 18: 37.695; 29: 1.2; 30: 2.7; 31: 8.6; 32: 9.9 | 10 | 10 | [23 empty] | 10 | 10 | 14 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 41 | 53 | 35 |  |  |  | 9.17
| 11 | 152 |  | 140 |  | 148 |  |  |  | 8 | [13 empty] | 11 | 11 | 145 | 153 | 148 |  |  | 7 | [7 empty] | 210 | 370 | 0.080373 | 0.079449 | 5.241 | 8.398 | 11 | 11 | [15 empty] | 3.31 | 4.06 | 4.06 | 4.43 | 4.02 |  |  |  | 18 | 7.7 | 6.7 | 7 | 6.7 | 6.4 | 6.6 | 0.38 |  | 160 | 11 | 11 | 88 | 88 | 102 | 47 | 88 | 59 | 67.05% | 100.8 | 1.1455 | 2.1 | 3.7 | 4 | 520 |  | A | 54.3 | 94.6593 | 51.4 | 397.2 | 29.2 | 14.2 | 12.7 | 13.6 | 11 | 11 | 162 | 162 | 10400 |  |  | 56.8 | 121.7 | 99.9 | 56.8 | 68 | 47 |  |  |  |  | 108 | 970 | 11 | 0.45 | 11 | 11 |  | 124.8 | 124.8 | 57.5119 |  |  | 227.9 | 683.7 | [6 empty] | Rain | 11 | 11 | 1: 0.11; 2: 0; 3: 30.48; 4: 39.9; 8: 0.11; 9: 0; 10: 28.7; 11: 36.4; 15: 0.11; 16: 0; 17: 29.857; 18: 38.675; 29: 1.43; 30: 2.24; 31: 9; 32: 10.3 | 11 | 11 | [23 empty] | 11 | 11 | 14 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 34 | 53 | 28 |  |  |  | 5.17
| 12 | 170 |  | 148 |  | 162 |  |  |  | 8 | [13 empty] | 12 | 12 | 140 | 137 | 139 |  |  | 5 | [7 empty] | 220 | 390 | 0.07946 | 0.078546 | 5.2433 | 10.5372 | 12 | 12 | [15 empty] | 3.96 | 3.85 | 3.67 | 4.19 | 4.96 |  |  |  | 18 | 7.1 | 6.7 | 6.9 | 6.9 | 6.5 | 6.7 | 0.48 |  | 48 | 12 | 12 | 87 | 87 | 104 | 44 | 87 | 59 | 67.82% | 97.7 | 1.123 | 2.1 | 3.7 | 4 | 510 |  |  | 58.8 | 95.068 | 55.9 | 397.2 | 28.9 | 14.4 | 12.9 | 13.7 | 12 | 12 |  | 162 | 10400 |  |  | 46 | 98.5 | 80.9 | 46 | 55.1 | 38.1 |  |  |  |  | 104 | 880 | 10.1 | 0.45 | 12 | 12 |  | 128 | 128 | 56.2159 |  |  | 227.9 | 683.7 | [6 empty] | Clear | 12 | 12 | 1: 0.12; 2: 0.03; 3: 30.6; 4: 39.1; 8: 0.12; 9: 0; 10: 30.7; 11: 38.1; 15: 0.12; 16: 0.0195; 17: 30.635; 18: 38.75; 29: 1.45; 30: 1.73; 31: 9; 32: 10.1 | 12 | 12 | [23 empty] | 12 | 12 | 14 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 33 | 53 | 27 |  |  |  | 5.23
| 13 | 180 |  | 184 |  | 181 |  | 94 | 74 | 8 |  | 2600 | 2700 | 2300 | 2600 | 6780 |  | 5560 |  | 1.2381 | 0.77143 |  |  | 13 | 13 | 155 | 154 | 155 |  |  | 5 | [7 empty] | 210 | 350 | 0.1451 | 0.12688 | 2.8795 | 6.6115 | 13 | 13 | [15 empty] | 4.04 | 4.03 | 3.86 | 4.17 | 3.96 |  |  |  | 18 | 7.2 | 6.3 | 6.8 | 6.9 | 6.6 | 6.7 | 0.41 |  | 104 | 13 | 13 | 87 | 87 | 106 | 44 | 87 | 59 | 67.82% | 98.8 | 1.1356 | 2.1 | 3.7 | 4 | 510 | 1 | E | 65.7 | 95.586 | 62.8 | 227 | 31.2 | 6.4 | 9.2 | 7.3 | 13 | 13 |  | 0 | 0 |  |  | 43.9 | 94 | 77.2 | 43.9 | 52.5 | 36.3 |  |  |  |  | 107 | 870 | 10 | 0.44 | 13 | 13 |  | 147.2 | 147.2 | 56.3719 |  |  | 227.9 | 683.7 | [6 empty] | Clear | 13 | 13 | 1: 0.05; 2: 0.08; 3: 31.21; 4: 43; 8: 0.05; 9: 0.05; 10: 31; 11: 39.6; 15: 0.05; 16: 0.0695; 17: 31.1365; 18: 41.81; 29: 1.27; 30: 3.04; 31: 7.9; 32: 9.5 | 13 | 13 | [23 empty] | 13 | 13 | 14 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 26 | 40 | 7 |  |  |  | 5.28
| 14 | 224 | 78.6 | 220 | 81.8 | 223 | 79.7 | 70 | 90 | 24 | 220 | 2500 | 2900 | 4000 | 3900 | 1760* | 80.7 | 4840 | 84.3 | 1.4706 | 0.90625 |  |  | 14 | 14 | 89 | 95 | 91 | 77 | 92 | 11 | 4540 | 2.9 | 85.8 | 1.5 | 68.3 | 59% |  | 170 | 320 | 0.11458 | 0.14042 | 4.3752 | 7.7337 | 14 | 14 | 170 |  | 380 | 190 | 320 | 3100 |  | 3500 | 3100 | 3600 | 6.98 |  | 7.1 | 6.99 | 7.06 | 4.08 | 3.89 | 3.56 | 3.96 | 3.52 |  |  |  | 16 | 7.6 | 6.8 | 7.1 | 6.8 | 6.5 | 6.6 | 0.21 | > | 4000 | 14 | 14 | 136 | 89 | 236 | 46 | 135 | 60 | 44.12% | 101.2 | 0.74963 | 1.3 | 2.8 | 2.6 | 790 | 1.2 |  | 126.5 | 89.249 | 112.9 | 375.1 | 43.9 | 9.6 | 7.3 | 8.5 | 14 | 14 | 918 | 486 | 31100 |  |  | 86.3 | 157.7 | 135.3 | 86.3 | 81.6 | 55.7 |  |  |  |  | 104 | 1950 | 14.3 | 0.51 | 14 | 14 |  | 105.6 | 105.6 | 56.6921 |  |  | 227.9 | 683.7 | [6 empty] | Rain | 14 | 14 | 1: 0.07; 2: 0.42; 3: 18.21; 4: 29.5; 8: 0.09; 9: 0.35; 10: 17.6; 11: 27.4; 15: 0.077; 16: 0.3955; 17: 17.9965; 18: 28.765; 29: 0.86; 30: 1.84; 31: 8.7; 32: 12 | 14 | 14 | [23 empty] | 14 | 14 | 14 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 38 | 98 | 76 |  |  |  | 8.94
| 15 | 156 |  | 162 |  | 158 |  | 120 | 88 | 15 | 330 | 2700 | 2400 | 4200 | 4100 | 6620 |  | 6660 |  | 1.9286 | 0.96 |  |  | 15 | 15 | 108 | 152 | 123 | 54 | 66 | 6 | 3220 | 3.5 | 82.4 | 1.8 | 68.2 | 57% |  | 140 | 250 | 0.054422 | 0.068138 | 5.1633 | 7.3611 | 15 | 15 | [15 empty] | 4.79 | 4.6 | 4.85 | 5.6 | 4.26 | 1520 | 1190 | 1400 | 18 | 7.2 | 6.7 | 7 | 6.8 | 6.4 | 6.7 | 0.23 |  | 156 | 15 | 15 | 96 | 96 | 123 | 33 | 96 | 58 | 60.42% | 95.4 | 0.99375 | 1.9 | 3.5 | 3.7 | 570 | 1.4 | R | 63.3 | 90.5213 | 57.3 | 394.1 | 42.9 | 8.3 | 11 | 9.2 | 15 | 15 | 270 | 324 | 20700 |  |  | 59.2 | 130.5 | 107.5 | 59.2 | 67.1 | 45.8 |  |  |  |  | 102 | 1070 | 11.1 | 0.45 | 15 | 15 |  | 166.4 | 166.4 | 55.0399 |  |  | 227.9 | 683.7 | [6 empty] | Clear | 15 | 15 | 0.21 | 0.01 | 20.76 | 33.2 | 2.23 | 4.04 | 375 | 0.2 | 0.06 | 20.8 | 32.8 | 2.2 | 3.84 | 333 | 0.2065 | 0.0275 | 20.774 | 33.06 | 2.2195 | 3.97 | 360.3 | 0.18 | 0.09 | 17.4 | 24.4 | 2.12 | 4.01 | 213 | 1.39 | 2.54 | 7 | 9.8 | 3.32 | 6.45 | 84 | 15 | 15 | [23 empty] | 15 | 15 | 14 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 32 | 26 | 0 |  |  |  | 8.63
| 16 | 144 | 86.1 | 162 | 82.7 | 150 | 84.9 | 74 | 68 | 6 | 880 | 2900 | 2800 | 3700 | 4200 | 7700 | 78.2 | 6840 | 78.7 | 1.5263 | 0.96552 |  |  | 16 | 16 | 129 | 146 | 135 | 85 | 68 | 3 | 3680 | 3.91 | 74.5 | 1.8 | 64.4 | 60% |  | 190 | 290 | 0.087111 | 0.061392 | 4.1339 | 8.7113 | 16 | 16 | [15 empty] | 4.33 | 4.15 | 3.96 | 3.55 | 4.42 |  |  |  | 19 | 7.3 | 6.7 | 7 | 6.9 | 6.4 | 6.6 | 0.43 |  | 30 | 16 | 16 | 86 | 86 | 103 | 54 | 86 | 58 | 67.44% | 96.3 | 1.1198 | 2.1 | 3.8 | 4.1 | 510 | 1.2 |  | 53.8 | 95.9108 | 51.6 | 365.7 | 25.7 | 13.2 | 16.3* | 14.2 | 16 | 16 | 162 | 324 | 20700 |  |  | 81.9 | 201.7 | 150.3 | 81.9 | 92.9 | 59.8 |  |  |  |  | 100 | 1120 | 13 | 0.46 | 16 | 16 |  | 124.8 | 124.8 | 54.3641 |  |  | 227.9 | 683.7 | [6 empty] | Rain | 16 | 16 | 1: 0.07; 2: 0.09; 3: 28.66; 4: 37.23; 8: 0.15; 9: 0; 10: 25.6; 11: 34.7; 15: 0.098; 16: 0.0585; 17: 27.589; 18: 36.3445; 29: 1.5; 30: 3.11; 31: 8; 32: 8.6 | 16 | 16 | [23 empty] | 16 | 16 | 14 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 25 | 29 | -4 |  |  |  | 8.6
| 17 | 182 |  | 156 |  | 173 |  | 74 | 102 | 6 | 160 | 3000 | 3200 | 4500 | 4400 | 6700 |  | 5600 |  | 1.3043 | 0.91429 |  |  | 17 | 17 | 143 | 142 | 143 | 82 | 115 | 3 | 2530 | 3.64 | 79.8 | 1.75 | 67.4 | 59% |  | 230 | 350 | 0.0699 | 0.10026 | 5.7544 | 9.641 | 17 | 17 | 210 |  | 440 | 200 | 370 | 3500 |  | 3400 | 2900 | 3500 | 7.2 |  | 7.01 | 7.14 | 7.1 | 3.95 | 4.06 | 4.09 | 2.64 | 4.43 |  |  |  | 19 | 7.3 | 6.7 | 6.9 | 6.7 | 6.2 | 6.5 | 0.32 |  | 34 | 17 | 17 | 87 | 87 | 105 | 52 | 87 | 62 | 71.26% | 93.5 | 1.0747 | 2.1 | 3.7 | 4 | 510 | 1.1 | A | 62.8 | 96.4968 | 60.6 | 422.4 | 30.9 | 15.9* | 11.2 | 13.7 | 17 | 17 | 324 | 162 | 10400 |  |  | 62.4 | 143.1 | 114.2 | 62.4 | 68.8 | 46.4 |  |  |  |  | 102 | 1380 | 15.9 | 0.46 | 17 | 17 |  | 131.2 | 131.2 | 52.2079 |  | See | 227.9 | 683.7 | [6 empty] | Clear | 17 | 17 | 1: 0.02; 2: 0.12; 3: 29.87; 4: 39.2; 8: 0.02; 9: 0.09; 10: 31.8; 11: 36.2; 15: 0.02; 16: 0.1095; 17: 30.5455; 18: 38.15; 29: 1.12; 30: 2.97; 31: 7.7; 32: 8.6 | 17 | 17 | [23 empty] | 17 | 17 | 14 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 34 | 56 | 28 |  |  |  | 8.74
| 18 | 140 |  | 131 |  | 137 |  |  |  | 7 | [13 empty] | 18 | 18 | 140 | 152 | 144 |  |  | 3 | [7 empty] | 200 | 350 | 0.07672 | 0.075838 | 5.2747 | 8.4096 | 18 | 18 | [15 empty] | 4.04 | 4.06 | 3.17 | 3.54 | 4.23 |  |  |  | 18 | 7.3 | 6.7 | 6.9 | 6.6 | 6.1 | 6.4 | 0.28 |  | 38 | 18 | 18 | 84 | 84 | 95 | 44 | 84 | 62 | 73.81% | 95.9 | 1.1417 | 2 | 3.7 | 4.2 | 490 |  |  | 48 | 94.7917 | 45.5 | 397.2 | 27.9 | 14.9 | 13.3 | 14.2 | 18 | 18 |  | 162 | 10400 |  |  | 42.5 | 91 | 74.7 | 42.5 | 50.9 | 35.2 |  |  |  |  | 96 | 770 | 9.2 | 0.47 | 18 | 18 |  | 128 | 128 | 54.5122 | N | Notes | 227.9 | 683.7 | [6 empty] | Clear | 18 | 18 | 1: 0.02; 2: 0.11; 3: 28.78; 4: 39.6; 8: 0.02; 9: 0.08; 10: 28.2; 11: 37; 15: 0.02; 16: 0.0995; 17: 28.577; 18: 38.69; 29: 1.24; 30: 3.39; 31: 7.7; 32: 8.5 | 18 | 18 | [23 empty] | 18 | 18 | 13 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 32 | 51 | 21 |  |  |  | 9.44
| 19 | 131 |  | 146 |  | 136 |  |  |  | 6 | [13 empty] | 19 | 19 | 146 | 166 | 153 |  |  | 4 | [7 empty] | 210 | 380 | 0.07946 | 0.078546 | 5.294 | 8.4589 | 19 | 19 | [15 empty] | 3.91 | 3.51 | 3.6 | 3.55 | 4.42 |  |  |  | 18 | 6.9 | 6.5 | 6.7 | 6.8 | 6.3 | 6.5 | 0.45 |  | 7 | 19 | 19 | 87 | 87 | 110 | 44 | 87 | 62 | 71.26% | 100.4 | 1.154 | 1.9 | 3.7 | 4 | 510 |  | T | 49.3 | 95.5375 | 47.1 | 397.2 | 28.9 | 14.4 | 12.9 | 13.7 | 19 | 19 |  | 0 | 0 |  |  | 51.6 | 110.5 | 90.7 | 51.6 | 61.8 | 42.7 |  |  |  |  | 96 | 1170 | 13.4 | 0.45 | 19 | 19 |  | 131.2 | 131.2 | 55.1839 | O | Below | 227.9 | 683.7 | [6 empty] | Clear | 19 | 19 | 1: 0; 2: 0.12; 3: 32.06; 4: 41.8; 8: 0; 9: 0.09; 10: 30.7; 11: 39.9; 15: 0; 16: 0.1095; 17: 31.584; 18: 41.135; 29: 1.1; 30: 2.89; 31: 8.2; 32: 8.8 | 19 | 19 | [23 empty] | 19 | 19 | 13 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 33 | 53 | 24 |  |  |  | 5.23
| 20 | 128 |  | 132 |  | 129 |  | 82 | 92 | 8 |  | 2700 | 3100 | 4200 | 6100 | 2940 |  | 5480 |  | 1.35 | 0.81579 |  |  | 20 | 20 | 183 | 180 | 182 |  |  | 4 | [7 empty] | 200 | 380 | 0.085853 | 0.058432 | 11.5* | 182.9* | 20 | 20 | [15 empty] | 2.78 | 3.85 | 2.55 | 3.61 | 4.24 |  |  |  | 18 | 7.5 | 6.6 | 6.8 | 6.6 | 6.4 | 6.5 | 0.47 |  | 4 | 20 | 20 | 94 | 94 | 118 | 42 | 94 | 63 | 67.02% | 98.8 | 1.0511 | 1.8 | 3.5 | 3.7 | 550 | 1.1 |  | 50.6 | 93.8735 | 47.5 | 457.1 | 33.7 | 12.4 | 16.0* | 13.6 | 20 | 20 | 162 | 162 | 10400 |  |  | 49.9 | 106.9 | 87.8 | 49.9 | 59.7 | 41.3 |  |  |  |  | 97 | 1020 | 10.9 | 0.4 | 20 | 20 |  | 134.4 | 134.4 | 55.7239 |  |  | 227.9 | 683.7 | [6 empty] | Snow | 20 | 20 | 1: 0; 2: 0.11; 3: 31.69; 4: 40.5; 8: 0; 9: 0.09; 10: 30.1; 11: 37.3; 15: 0; 16: 0.103; 17: 31.1335; 18: 39.38; 29: 1.09; 30: 2.45; 31: 9.3; 32: 10.1 | 20 | 20 | [23 empty] | 20 | 20 | 13 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 513 | 59 | 509 |  |  |  | 8.79
| 21 | 138 | 84.1 | 156 | 84.6 | 144 | 84.3 | 224* | 66 | 10 | 400 | 3300 | 3700 | 4500 | 4700 | 7920 | 82.6 | 3820 | 84.3 | 1.0645 | 0.925 |  |  | 21 | 21 | 120 | 131 | 124 | 124 | 64 | 6 | 2840 | 2.73 | 82.5 | 1.92 | 68.8 | 41% |  | 310 | 400 | 0.1215 | 0.06004 | 4.7806 | 106.3* | 21 | 21 | 250 |  | 420 | 150 | 220 | 3100 |  | 3000 | 2900 | 3000 | 7 |  | 7 | 7 | 7 | 3.76 | 3.58 | 3.58 | 3.74 | 3.62 |  |  |  | 18 | 7.2 | 6.6 | 6.8 | 6.7 | 6.4 | 6.6 | 0.34 |  | 38 | 21 | 21 | 100 | 94 | 121 | 50 | 100 | 63 | 63% | 98.8 | 0.988 | 1.7 | 3.3 | 3.5 | 590 | 1 | I | 60 | 93 | 55.8 | 431.9 | 30 | 13.4 | 16.2* | 14.4 | 21 | 21 |  | 486 | 31100 |  |  | 104.2 | 179.2 | 147.8 | 104.2 | 126 | 86.7 |  |  |  |  | 98 | 1070 | 10.7 | 0.46 | 21 | 21 |  | 137.6 | 137.6 | 54.7639 | M |  | 227.9 | 683.7 | [6 empty] | Snow/Clear | 21 | 21 | 1: 0.02; 2: 0.13; 3: 28.66; 4: 38.8; 8: 0.03; 9: 0.1; 10: 26.6; 11: 34.4; 15: 0.0235; 16: 0.1195; 17: 27.939; 18: 37.26; 29: 1; 30: 1.85; 31: 9.4; 32: 10 | 21 | 21 | [23 empty] | 21 | 21 | 13 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 35 | 1514 | 1486 |  |  |  | 5.37
| 22 | 138 |  | 150 |  | 142 |  | 82 | 88 | 9 | 142 | 3900 | 3400 | 4900 | 4300 | 6540 |  | 5000 |  | 1.3 | 0.75556 |  |  | 22 | 22 | 161 | 174 | 166 | 82 | 96 | 5 | 3360 | 2.78 | 84.3 | 1.9 | 67.3 | 45% |  | 300 | 450 | 0.068621 | 0.091547 | 6.3 | 9.0462 | 22 | 22 | [15 empty] | 3.88 | 3.84 | 3.19 | 3.76 | 4.03 | 111 | 224 | 150 | 18 | 7.3 | 6.4 | 6.8 | 6.7 | 6.4 | 6.6 | 0.44 |  | 13 | 22 | 22 | 93 | 93 | 149 | 49 | 93 | 61 | 65.59% | 98.8 | 1.0624 | 1.8 | 3.5 | 3.8 | 550 | 1 |  | 55.1 | 93.6479 | 51.6 | 444.5 | 32.7 | 14.6 | 11.9 | 13.6 | 22 | 22 |  | 324 | 20700 |  |  | 91.7 | 160.6 | 135.4 | 91.7 | 109.8 | 73.9 |  |  |  |  | 99 | 780 | 8.4 | 0.45 | 22 | 22 |  | 128 | 128 | 54.6202 | E |  | 227.9 | 683.7 | [6 empty] | Clear | 22 | 22 | 1: 0; 2: 0.13; 3: 32.3; 4: 40.9; 8: 0.01; 9: 0.1; 10: 30.8; 11: 39.3; 15: 0.0035; 16: 0.1195; 17: 31.775; 18: 40.34; 22: 0; 23: 0.05; 24: 24; 29: 1.34; 30: 2.52; 31: 7; 32: 8.4 | 22 | 22 | [23 empty] | 22 | 22 | 13 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 67 | 96 | 102 |  |  |  | 8.78
| 23 | 164 | 86.6 | 162 | 84 | 163 | 85.7 | 102 | 82 | 9 | 360 | 3300 | 3300 | 5300 | 4500 | 8580 | 80 | 5680 | 79.2 | 1 | 1.2222 |  |  | 23 | 23 | 162 | 161 | 162 | 127 | 83 | 6 | 2070 | 2.98 | 81.8 | 1.68 | 68.2 | 53% |  | 330 | 270 | 0.098258 | 0.075632 | 5.2534 | 8.8481 | 23 | 23 | [15 empty] | 2.91 | 3.69 | 2.16 | 2.5 | 3.93 |  |  |  | 19 | 7.2 | 6.3 | 6.7 | 6.6 | 6.4 | 6.5 | 0.41 |  | 37 | 23 | 23 | 93 | 93 | 113 | 57 | 93 | 61 | 65.59% | 96.5 | 1.0376 | 1.8 | 3.5 | 3.8 | 550 | 1.1 | O | 63.2 | 94.462 | 59.7 | 476 | 36.5 | 12.7 | 13.4 | 13 | 23 | 23 | 162 | 0 | 0 |  |  | 59.4 | 111.5 | 91.2 | 59.4 | 62.9 | 42.9 |  |  |  |  | 101 | 1660 | 17.8 | 0.5 | 23 | 23 |  | 137.6 | 137.6 | 54.912 | T |  | 227.9 | 683.7 | [6 empty] | Clear | 23 | 23 | 1: 0; 2: 0.12; 3: 31.94; 4: 38.6; 8: 0; 9: 0.08; 10: 32.2; 11: 40; 15: 0; 16: 0.106; 17: 32.031; 18: 39.09; 29: 1.09; 30: 2.2; 31: 8.1; 32: 8.7 | 23 | 23 | [23 empty] | 23 | 23 | 13 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 28 | 63 | 30 |  |  |  | 8.9
| 24 | 130 |  | 150 |  | 137 |  | 82 | 76 | 8 | 1130 | 2800 | 3100 | 4000 | 3700 | 6000 |  | 4800 |  | 1.037 | 0.67391 |  |  | 24 | 24 | 179 | 167 | 175 | 96 | 105 | 5 | 5180 | 3.06 | 82.9 | 2.02 | 69.9 | 44% |  | 270 | 460 | 0.088889 | 0.10511 | 5.6391 | 7.2101 | 24 | 24 | 180 |  | 170 | 120 | 320 | 3100 |  | 3000 | 2200 | 2900 | 7.17 |  | 7.12 | 7.09 | 7 | 3.92 | 3.55 | 3.54 | 4.72 | 3.94 |  |  |  | 18 | 7.6 | 6.5 | 6.9 | 6.6 | 6.2 | 6.5 | 0.23 |  | 117 | 24 | 24 | 84 | 84 | 105 | 48 | 84 | 61 | 72.62% | 93.5 | 1.1131 | 2 | 3.8 | 4.2 | 490 | 0.9 |  | 48 | 94.1667 | 45.2 | 368.8 | 27.9 | 13.2 | 13.1 | 13.2 | 24 | 24 | 162 | 162 | 10400 |  |  | 44.7 | 86.2 | 71.5 | 44.7 | 56.9 | 39.8 |  |  |  |  | 100 | 1220 | 14.5 | 0.44 | 24 | 24 |  | 128 | 128 | 56.88 | E |  | 227.9 | 683.7 | [6 empty] | Clear | 24 | 24 | 1: 0; 2: 0.12; 3: 31.69; 4: 40.2; 8: 0; 9: 0.07; 10: 31.9; 11: 38.7; 15: 0; 16: 0.1025; 17: 31.7635; 18: 39.675; 29: 1.43; 30: 2.65; 31: 6.8; 32: 7.5 | 24 | 24 | [23 empty] | 24 | 24 | 13 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 36 | 75 | 50 |  |  |  | 8.57
| 25 | 136 |  | 190 |  | 155 |  |  |  | 9 | [13 empty] | 25 | 25 | 148 | 165 | 154 |  |  | 4 | [7 empty] | 480 | 420 | 0.077633 | 0.076741 | 5.2235 | 7.8311 | 25 | 25 | [15 empty] | 3.59 | 3.97 | 3.38 | 3.42 | 4.05 |  |  |  | 18 | 7.1 | 6.4 | 6.7 | 6.6 | 6.3 | 6.5 | 0.23 |  | 40 | 25 | 25 | 85 | 84 | 136 | 36 | 85 | 61 | 71.76% | 90.7 | 1.0671 | 2 | 3.7 | 4.1 | 500 |  | N | 54.9 | 94.1712 | 51.7 | 397.2 | 28.2 | 14.7 | 13.2 | 14.1 | 25 | 25 | 162 | 162 | 10400 |  |  | 51.6 | 110.5 | 90.7 | 51.6 | 61.8 | 42.7 |  |  |  |  | 104 | 1270 | 14.9 | 0.44 | 25 | 25 |  | 115.2 | 115.2 | 55.0402 | R |  | 227.9 | 683.7 | [6 empty] | Rain | 25 | 25 | 1: 0; 2: 0.1; 3: 30.48; 4: 39.9; 8: 0; 9: 0.06; 10: 27.9; 11: 38.7; 15: 0; 16: 0.086; 17: 29.577; 18: 39.48; 29: 1.14; 30: 2.16; 31: 8.1; 32: 9 | 25 | 25 | [23 empty] | 25 | 25 | 13 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 33 | 52 | 24 |  |  |  | 8.75
| 26 | 154 |  | 130 |  | 146 |  |  |  | 9 | [13 empty] | 26 | 26 | 133 | 137 | 134 |  |  | 4 | [7 empty] | 510 | 590 | 0.075806 | 0.074935 | 5.2287 | 7.7777 | 26 | 26 | [15 empty] | 3.79 | 3.39 | 3.28 | 2.93 | 4.28 |  |  |  | 19 | 7 | 6.6 | 6.8 | 6.6 | 6.4 | 6.5 | 0.53 |  | 58 | 26 | 26 | 83 | 83 | 108 | 55 | 83 | 60 | 72.29% | 92.5 | 1.1145 | 2 | 3.8 | 4.2 | 490 |  |  | 50.5 | 93.8614 | 47.4 | 397.2 | 27.6 | 15.1 | 13.5 | 14.4 | 26 | 26 | 486 | 162 | 10400 |  |  | 64.5 | 138.2 | 113.5 | 64.5 | 77.2 | 53.3 |  |  |  |  | 104 | 1120 | 13.5 | 0.46 | 26 | 26 |  | 128 | 128 | 55.884 |  |  | 227.9 | 683.7 | [6 empty] | Clear | 26 | 26 | 1: 0.03; 2: 0.08; 3: 32.18; 4: 41.9; 8: 0.03; 9: 0.06; 10: 30.6; 11: 38.1; 15: 0.03; 16: 0.073; 17: 31.627; 18: 40.57; 29: 1.19; 30: 1.88; 31: 9.9; 32: 10.2 | 26 | 26 | [23 empty] | 26 | 26 | 13 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 32 | 50 | 22 |  |  |  | 8.75
| 27 | 144 |  | 132 |  | 140 |  | 190* | 89 | 9 |  | 2600 | 3100 | 2900 | 3100 | 6900 |  | 10120* |  | 0.56522 | 0.49206 |  |  | 27 | 27 | 161 | 151 | 158 |  |  | 5 | [7 empty] | 460 | 630 | 0.11243 | 0.10397 | 3.5566 | 5.8726 | 27 | 27 | [15 empty] | 3.69 | 3.89 | 3.93 | 3.27 | 3.79 |  |  |  | 18 | 7.3 | 6.6 | 7 | 7.1 | 6.6 | 6.9 | 0.45 |  | 63 | 27 | 27 | 85 | 85 | 109 | 60 | 85 | 60 | 70.59% | 94.6 | 1.1129 | 2 | 3.8 | 4.1 | 500 | 0.5 |  | 49.6 | 93.5484 | 46.4 | 280.6 | 28.8 | 10.2 | 9.3 | 9.7 | 27 | 27 |  | 0 | 0 |  |  | 87 | 186.4 | 153 | 87 | 104.1 | 71.9 |  |  |  |  | 103 | 1220 | 14.4 | 0.44 | 27 | 27 |  | 147.2 | 147.2 | 55.5761 |  |  | 227.9 | 683.7 | [6 empty] | Clear | 27 | 27 | 1: 0.02; 2: 0.06; 3: 31.26; 4: 39.4; 8: 0.04; 9: 0.04; 10: 30.4; 11: 38.4; 15: 0.027; 16: 0.053; 17: 30.959; 18: 39.05; 29: 1.02; 30: 2.64; 31: 7.6; 32: 7.8 | 27 | 27 | [23 empty] | 27 | 27 | 13 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 25 | 56 | 21 |  |  |  | 6.46
| 28 | 160 | 80 | 202 | 81.2 | 175 | 80.4 | 62 | 132 | 34 | 1390 | 3300 | 2700 | 4500 | 3400 | 7140 | 81 | 4180 | 82.3 | 0.73333 | 0.79412 |  |  | 28 | 28 | 68 | 77 | 71 | 67 | 68 | 11 | 4620 | 3.08 | 82.1 | 1.9 | 71.4 | 46% |  | 450 | 340 | 0.085998 | 0.11552 | 4.4766 | 5.3218 | 28 | 28 | 250 |  | 400 | 140 | 300 | 2800 |  | 2600 | 3000 | 2900 | 7 |  | 6.9 | 7 | 7 | 3.29 | 4.4 | 2.42 | 5.08 | 2.47 |  |  |  | 17 | 7.2 | 6.6 | 6.9 | 7 | 6.1 | 6.5 | 0.22 | > | 4000 | 28 | 28 | 131 | 85 | 200 | 53 | 131 | 60 | 45.8% | 92.9 | 0.70916 | 1.3 | 2.8 | 2.7 | 770 | 0.8 |  | 95.6 | 80.5439 | 77 | 390.9 | 49.2 | 12.6 | 4.5 | 7.9 | 28 | 28 | 324 | 324 | 20700 |  |  | 41.4 | 80.3 | 65.9 | 41.4 | 49.6 | 35.4 |  |  |  |  | 100 | 2330 | 17.8 | 0.47 | 28 | 28 |  | 131.2 | 131.2 | 54.7039 |  |  | 227.9 | 683.7 | [6 empty] | Rain | 28 | 28 | 1: 0.11; 2: 0.34; 3: 17.85; 4: 27.6; 8: 0.06; 9: 0.24; 10: 17.7; 11: 26.2; 15: 0.0925; 16: 0.305; 17: 17.7975; 18: 27.11; 29: 0.96; 30: 2; 31: 6.9; 32: 9.8 | 28 | 28 | [23 empty] | 28 | 28 | 13 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 55 | 114 | 109
| 29 | 151 |  | 144 |  | 149 |  | 80 | 96 | 7 | 3990 | 3400 | 3000 | 4800 | 4500 | 6980 |  | 5220 |  | 0.64151 | 0.69767 |  |  | 29 | 29 | 136 | 150 | 141 | 76 | 80 | 3 | 5500 | 3.55 | 83 | 1.35 | 72.2 | 67% |  | 530 | 430 | 0.057246 | 0.064276 | 5.8821 | 8.0139 | 29 | 29 | [15 empty] | 4.19 | 3.98 | 3.67 | 3.72 | 4.41 | 98 | 225 | 140 | 18 | 7.2 | 6.7 | 7 | 6.9 | 6.4 | 6.6 | 0.29 |  | 120 | 29 | 29 | 82 | 82 | 94 | 57 | 82 | 59 | 71.95% | 88.4 | 1.078 | 2.1 | 3.9 | 4.3 | 480 | 0.7 |  | 50.9 | 95.2849 | 48.5 | 444.5 | 29.5 | 16.6* | 13 | 15.1 | 29 | 29 | 1026 | 486 | 31100 |  |  | 71.5 | 159.9 | 132.7 | 71.5 | 60.8 | 43.9 |  |  |  |  | 102 | 1080 | 13.2 | 0.43 | 29 | 29 |  | 140.8 | 140.8 | 55.6481 |  |  | 227.9 | 683.7 | [6 empty] | Clear | 29 | 29 | 1: 0.14; 2: 0.09; 3: 28.41; 4: 40.7; 8: 0.13; 9: 0.05; 10: 27.4; 11: 36.8; 15: 0.1365; 16: 0.076; 17: 28.0565; 18: 39.335; 22: 0.02; 23: 0.03; 24: 22.6; 29: 1.44; 30: 3.06; 31: 5.3; 32: 6.5 | 29 | 29 | [23 empty] | 29 | 29 | 13 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 38 | 54 | 33
| 30 | 136 | 83.8 | 146 | 79.5 | 140 | 82.3 | 64 | 82 | 6 | 2710 | 3600 | 3200 | 4500 | 4000 | 7560 | 78.3 | 5220 | 77 | 0.75 | 0.8 |  |  | 30 | 30 | 139 | 157 | 145 | 81 | 80 | 2 | 3610 | 3.6 | 80.6 | 1.55 | 69.2 | 63% |  | 480 | 400 | 0.065873 | 0.073192 | 5.1231 | 6.7444 | 30 | 30 | [15 empty] | 3.94 | 3.93 | 2.28 | 4.31 | 4.38 |  |  |  | 17 | 7.3 | 6.6 | 6.8 | 6.8 | 6.2 | 6.5 | 0.28 |  | 9 | 30 | 30 | 83 | 83 | 105 | 54 | 83 | 59 | 71.08% | 93.5 | 1.1265 | 2 | 3.8 | 4.2 | 490 | 0.8 |  | 48.5 | 95.6701 | 46.4 | 409.8 | 24.6 | 19.2* | 13.3 | 16.7 | 30 | 30 |  | 0 | 0 |  |  | 128 | 290.3 | 234 | 128 | 125 | 86.5 |  |  |  |  | 103 | 1610 | 19.4 | 0.43 | 30 | 30 |  | 137.6 | 137.6 | 56.0801 |  |  | 227.9 | 683.7 | [6 empty] | Clear | 30 | 30 | 1: 0.14; 2: 0.02; 3: 30.36; 4: 40.1; 8: 0.17; 9: 0; 10: 29.8; 11: 38; 15: 0.1505; 16: 0.013; 17: 30.164; 18: 39.365; 29: 1.94; 30: 3.32; 31: 4.7; 32: 6.1 | 30 | 30 | [23 empty] | 30 | 30 | 13 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 37 | 64 | 42
| 31 | 120 |  | 132 |  | 124 |  | 50 | 76 | 6 | 134 | 3700 | 3200 | 4500 | 4200 | 6960 |  | 4700 |  | 0.90244 | 0.94118 |  |  | 31 | 31 | 151 | 149 | 150 | 88 | 93 | 3 | 2210 | 2.97 | 83.1 | 1.89 | 77.6 | 41% |  | 410 | 340 | 0.070704 | 0.080058 | 5.5545 | 8.3003 | 31 | 31 | 300 |  | 290 | 360 | 1040 | 3100 |  | 3200 | 2800 | 800 | 7.2 |  | 7.4 | 7.2 | 5.88 | 3.95 | 3.9 | 3.61 | 2.57 | 4.46 |  |  |  | 19 | 7.3 | 6.5 | 6.8 | 6.6 | 6.1 | 6.4 | 0.46 |  | 18 | 31 | 31 | 82 | 82 | 99 | 50 | 82 | 58 | 70.73% | 88.8 | 1.0829 | 2.1 | 3.9 | 4.3 | 480 | 0.9 |  | 42.4 | 95.0472 | 40.3 | 416.1 | 20.7 | 24.9* | 15.3* | 20.1 | 31 | 31 |  | 486 | 31100 |  |  | 90.4 | 169.1 | 140.5 | 90.4 | 107.6 | 83.5 |  |  |  |  | 103 | 1260 | 15.4 | 0.42 | 31 | 31 |  | 124.8 | 124.8 | 54.9161 |  |  | 227.9 | 683.7 | [6 empty] | Clear | 31 | 31 | 1: 0.02; 2: 0.1; 3: 31.33; 4: 38.2; 8: 0.02; 9: 0.05; 10: 30; 11: 37; 15: 0.02; 16: 0.0825; 17: 30.8645; 18: 37.78; 29: 1.51; 30: 3.53; 31: 5.5; 32: 6.4 | 31 | 31 | [23 empty] | 31 | 31 | 13 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 46 | 85 | 73
| Avg | 148 | 82 | 151 | 81.4 | 149 | 81.8 | 76 | 85 | 12 | 680 | 3000 | 3000 | 4200 | 4200 | 6800 | 80 | 5400 | 80 | 1.2 | 0.8 |  |  | Avg | Avg | 141 | 148 | 144 | 87 | 86 | 6 | 2838.95 | 3.4 | 82.1 | 1.9 | 69.1 | 50% |  | 290 | 410 | 0.08 | 0.08 | 5.1 | 8.4 | Avg | Avg | 220 |  | 290 | 210 | 340 | 3200 |  | 3300 | 2800 | 3000 | 7.1 |  | 7.1 | 7.1 | 6.9 | 3.8 | 3.9 | 3.8 | 4.1 | 4.1 | 390 | 430 | 400 | 18 | 7.3 | 6.6 | 6.9 | 6.8 | 6.4 | 6.6 | 0.38 |  | 67 | AVG | Tot | 2828 | 2701 |  |  | 2827 |  |  | 2996.1 | [7 empty] | 1777 |  | 1625.3 | 12370 | 942.2 |  |  |  | Total | Total | 4806 | 6966 | 445800 | 0 | 0 | 2037.5 | 4314.8 | 3536.5 | 2037.5 | 2389.6 | 1652.3 | [5 empty] | 35720 |  |  | Total | Total | 0 | 4121.6 | 4121.6 | 1722.8405 | 28263 |  | 7064.9 | 21194.7 | 254 | 0 | 254 | 9787 | 9704 | 83 |  | Total | AVG | 0.07 | 0.11 | 28.8 | 38.3 | 2.45 | 4.32 | 374 | 0.07 | 0.08 | 28 | 36.6 | 2.39 | 4.15 | 348 | 0.07 | 0.1 | 28.5 | 37.7 | 2.43 | 4.26 | 365 | 0.05 | 0.04 | 22.4 | 27.9 | 2.34 | 4.37 | 223 | 1.19 | 2.55 | 8.7 | 9.9 | 2.3 | 3.97 | 66 | AVG | AVG | [23 empty] | AVG | Avg | 14 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 51.8065 | 105.3226
|  | NOTES: | [78 empty] | Avg | 91.2258 | 87.129 | 121.2903 | 48.5806 | 91.1935 | 59.4194 | 66.02% | 96.6 | 1.07 | 1.9742 | 3.6387 | 3.9 | 500 | 1 |  | 57.3 | 91.7448 | 52.429 | 399.0323 | 30.3935 | 12.5 | 11.7 | 13.6 | Avg | Avg | 320.4 | 224.7097 | 14380.6452 | 0 | 0 | 65.7258 | 139.1871 | 114.0806 | 65.7258 | 77.0839 | 53.3 |  |  |  |  | 103 | 1152 | 12.6 | 0.46 | Avg | Avg |  | 133 | 133 | 55.6 | [11 empty] | Avg
|  | SATURDAY AND SUNDAY SAMPLES ARE COMPOSITED PRIOR TO ANALYSIS | [10 empty] | Grit Analysis | [32 empty] | Dig. | Volatiles/Alkalinity Ratio |  |  |  |  | Alkalinity (mg/L) |  |  |  | CBOD (mg/L) | [9 empty] | Suspended Solids | [68 empty] | CHECK!!!!! | [9 empty] | 4: Total; 10: Total; 11: Remarks: | [42 empty] | *Dewatering shut down on January 4th for contract work
|  | EXCEPT FOR RAW AND FINAL SAMPLES WHICH ARE ANALYZED DAILY. | [10 empty] | No. 1 |  | No. 2 |  | No. 3 |  | No. 4 | [26 empty] | 3 | 0.06875 | [5 empty] | Prim |  | Prim |  | Prim | Prim |  | Prim | Prim |  |  |  |  | Raw | 149 | % Rem | [18 empty] | % | Dry | Per | Per |  | Water Consumption | [37 empty] | Special Remarks: | [14 empty] | 2: Average Total FLow; 4: Nitrogen; 5: Sludge Age:; 6: 13.6; 7: Days; 9: Flow; 10: Nitrogen
|  | STARRED VALUES ARE EXCLUDED FROM ALL CALCULATIONS. | [9 empty] | DATE | %SOL. | %VOL. | %SOL. | %VOL. | %SOL. | %VOL. | %SOL. | %VOL. | [25 empty] | 6 | 0.087879 |  |  |  |  | Date | N & S | Date | N & S | Date | North | South | Date | North | South |  |  |  |  | Primary | 80.5 | 45.97% | [13 empty] | Material |  |  | Cubic Feet |  | Solids | lbs | Day | MG |  | Meter (x1000 cuft) | [37 empty] | Note: | [14 empty] | 2: (MGD); 3: 91.2258; 4: lbs/day; 9: MGD; 10: lbs/day
|  | N/A INDICATES SCHEDULED ANALYSIS NOT DONE. | [9 empty] | 3/7/16 | 39.3 | 45.4 | 43.5 | 45.4 | 38.9 | 44.3 | [27 empty] | 7 | 0.075 |  |  |  |  | 3/7/16 | 166 | 3/28/16 | 143 | [10 empty] | Final | 12 | 92% |  |  | OTE | #VALUE! | [9 empty] | Rakings |  |  |  | 4806 | 50 | 120200 | 3880 | 45 |  |  | Meter 1 | Meter 2 | Meter 3 | [12 empty] | Digested Sludge cuft |  |  |  | Centrate cuft | [32 empty] | 2: Influent; 4: 28500; 5: Centrate
|  | BLANK SPACES INDICATE ANALYSIS NOT SCHEDULED. | [9 empty] | 3/14/16 | 42.9 | 41.2 | 41.4 | 42.4 | 41.8 | 43.7 | [27 empty] | 8 | 0.11333 |  |  |  |  | 3/14/16 | 164 | [12 empty] | CBOD | [5 empty] | #VALUE! | with out centrate NH3 | [8 empty] | Grit |  |  |  | 6966 | 85 | 445800 | 14380 | 160 |  | Date | Berrian | Berrian | Steinway | [12 empty] | To Boat |  | 2055227 |  | To Boat |  | 0 | [30 empty] | 2: Primary; 4: 21295; 5: Waste; 9: 2.2916
|  | SLUDGE (HEAVY METALS AND CATIONS) IS ON A DRY WEIGHT BASIS. | [9 empty] | 3/21/16 | 48.3 | 37.9 | 45.6 | 40.3 | 45.6 | 41 | [33 empty] | 3/21/16 | 146 | [12 empty] | Raw | 144 | % REM | [13 empty] | Scum |  |  |  | 0 | 60 | 0 | 0 | 5 |  | 2016-03-01 | Removed | 69846.2 | 83848.9 | [12 empty] | From Boat |  | 0 |  | From Boat | [17 empty] | 2. Digester gas produced is a calculated value -- with the assumption that 1 pound of volatile solids destroyed | [14 empty] | 2: Effluent; 4: 10400; 5: Sludge To Dewatering; 9: 0.49163
|  | OIL/GREASE ANALYSIS BY FREON EXTRACTION. | [9 empty] | 3/28/16 | 43.5 | 43.4 | 46.8 | 37.8 | 43.2 | 43.4 | [33 empty] | 3/28/16 | 143 | [12 empty] | Primary | 86.5 | 39.93% | [13 empty] | Exc Act Sludge |  |  |  | 2037500 | 3.3614 | 4314800 | 139187.0968 | 1526 |  | 2016-04-01 | Removed | 71965 | 84464.7 | [34 empty] | will produce 15 cubic feet of digester gas.
|  | HEAVY METAL AND CATION PERFORMED ON A MONTHLY COMPOSITE. | [63 empty] | Final | 6 | 96% | [13 empty] | Corr For Recir Digest Sludge | [9 empty] | Diff: | 0 | 2118.8 | 615.8 | [11 empty] | MONTHLY SLUDGE INVENTORY (cu ft) | [37 empty] | 15: Chemist in Charge: Nurum Islam
|  | pH DETERMINATIONS ARE MADE EVERY THREE HOURS. | [9 empty] | Average | 43.5 | 41.975 | 44.325 | 41.475 | 42.375 | 43.1 | #DIV/0! | #DIV/0! | [27 empty] | REMARKS: (1) | [33 empty] | Net Solids Removed | [5 empty] | 4880800 | 157447.0968 | 1736 |  | Total | 2734.6 | [13 empty] | by Storage volume |  | by Production | [20 empty] | Digester gas produced is a calculated value. One flare was in service since 1/30/2013 burning gas produced from Digester 6 & 7 (total of 4 primary digesters are in service during the month). Thre rest of digester gas produced was vented out. Started venting digester gas 100% on 11/14/13. | [14 empty] | 15: DATE:; 16: 2016-05-16 13:11
[48 empty] | (2) FECAL COLIFORM AVERAGE GEOMETRIC. | [22 empty] | Chemist in Charge: Nurum Islam | [35 empty] | Stor. 1st | 271216.5556 | Produced | 2037500
|  | DATE PRINTED: |  |  | 2016-05-16 13:11 |  |  | 42506.5493 | [12 empty] | Page 1 of 6 | [18 empty] | Page 2 of 6 | [7 empty] | (3) UNC = UNCOUNTABLE DUE TO EXCESS NON-FECAL COLIFORM COLONIES | [27 empty] | Page 3 of 6 | [6 empty] | Digester Operation |  |  |  | Total | [19 empty] | Stor. end | 359432.8945 | Boat | 2055227
[83 empty] | Cubic Feet Added |  |  |  | 2037500 | [21 empty] | To Dewatering | 0 | [34 empty] | 33: Page 1 of 2 | [23 empty] | Page 2 of 2
[83 empty] | Pounds Solids Added |  |  |  | 4314800 | [19 empty] | Stor chang | 88216.3389 | Difference | -17727
[83 empty] | Pounds Volatiles Destroyed |  |  |  | 1884200
[83 empty] | Gas Produced (Cu. Ft.) |  |  |  | 28263000 |  |  |  | According to gas meters, the gas produced = |  |  |  | 14089071 |  | cubic feed
[83 empty] | Gas (Cu. Ft./lb Vol destroyed) | [5 empty] | 15 |  | *Digester No. 7 gas production is not included, gas pipe leakage issue. | [38 empty] | Process Control Engineer: Yue Yue Guo
[102 empty] | Page 4 of 6 | [20 empty] | Page 5 of 6 | [6 empty] | Plant Superintendent: Eric Klee | [10 empty] | Page 6 of 6
Previous Month Update the links |  | Air | SRT (days) |  | SDI |  | sludge prd | chlorides |  | thickened sludge |  | Digester sludge |  | Aer Eff (mg/L) |  | Avg Aer |  | total nitrogen (mg/L) |  | total nitrogen (lb/d) |  | hypo dis | Cl2 res | Dig temp | Sludge age (days) |  | AerEff | Blower | caustic | glycerin | ferric | hypo for other | cake | polymer
|  | mcf/d | South | North | South | North | 1000cuft/d | High Level | Low Level | %sol | %vol | %sol | %vol | South | North | South | North | inf | eff | inf | eff | gpd | mg/L | F | South | North | DO | kwh | gpd | gpd | gpd | gpd | %sol | #/DT | [63 empty] | Flared
24 |  | 91 | 3.3834 | 5.1047 | 1.3333 | 0.96552 | 66.2 |  |  | 3.98 | 81 | 2.04 | 63.5 | 2800 | 2800 | 4500 | 4100 | 16.7 | 10.2 | 28969.824 | 17694.144 | 2150 | 0.47 | 102 | 8.9 | 5.5 | 6.82 | 52.8719 | 0 | 0 | 0 | 0 | [65 empty] | Reading from
25 |  | 90 | 5.4313 | 13.8052 | 1.2381 | 0.89655 | 43.9 |  |  | 4.07 | 77.7 | 1.78 | 67.1 | 2600 | 2600 | 5000 | 5600 | 29.4 | 10.2 | 25009.992 | 8676.936 | 970 | 0.5 | 105 | 22.2* | 16.8* | 6.9425 | 51.2902 | 0 | 0 | 0 | 1903.5 | [65 empty] | Gas meter
26 |  | 91.5 | 5.6162 | 12.7123 |  |  | 33.2 | [10 empty] | 40.3 | 15.3 | 28904.772 | 10973.772 | 590 | 0.43 | 105 | 16.1* | 14 | 4.695 | 51.4083 | 0 | 0 | 0 | 2115 | [64 empty] | DAY | cubic ft | [36 empty] | CHECK Fuel!!!!!
27 |  | 91.5 | 5.5192 | 12.8541 |  |  | 23.1 | [10 empty] | 39 | 16.5 | 29273.4 | 12384.9 | 730 | 0.4 | 105 | 15.3 | 13.4 | 3.9225 | 50.6769 | 0 | 0 | 0 | 1621.5 | [64 empty] | 1 | 203195
28 |  | 88.6 | 3.7269 | 10.8431 | 1.1818 | 1.0303 | 69.7 | [6 empty] | 2600 | 3400 | 2400 | 3500 | 39.3 | 18.2 | 29826.342 | 13812.708 | 530 | 0.46 | 105 | 8.7 | 11.5 | 3.9225 | 53.04 | 0 | 0 | 0 | 2467.5 | [64 empty] | 2 | 155488
29 |  | 86.5 | 5.4569 | 13.9368 | 1.2 | 0.45833 | 62.2 |  |  | 3.59 | 78.9 | 2 | 64 | 2400 | 3300 | 4100 | 4000 | 38 | 16.7 | 29156.64 | 12813.576 | 630 | 0.43 | 104 | 12.3 | 13.3 | 3.6175 | 57.1279 | 0 | 0 | 0 | 1904 | [64 empty] | 3 | 188881
30 | [96 empty] | 4 | 431274
31 | [96 empty] | 5 | 131994
[97 empty] | 6 | 301596
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | [16 empty] | 7 | 519209
FER only |  | Air | SRT (days) |  | SDI |  | sludge prd | chlorides |  | thickened sludge |  | Digester sludge |  | Aer Eff (mg/L) |  | Avg Aer |  | total nitrogen (mg/L) |  | total nitrogen (lb/d) |  | hypo dis | Cl2 res | Dig temp | Sludge age (days) |  | AerEff | Blower | caustic | glycerin | ferric | hypo for other | cake | polymer | [6 empty] | FER only |  | Air | SRT (days) |  | SDI |  | sludge prd | chlorides | thickened sludge |  | Digester sludge |  | Aer Eff (mg/L) |  | Avg Aer |  | total nitrogen (mg/L) |  | total nitrogen (lb/d) |  | hypo dis | Cl2 res | dig temp | Chloride | Sludge age (days) |  | AerEff | Blower | caustic | glycerin | ferric | hypo for other | cake | polymer | [21 empty] | 8 | 372162
|  | mcf/d | South | North | South | North | 1000cuft/d | High Level | Low Level | %sol | %vol | %sol | %vol | South | North | South | North | inf | eff | inf | eff | gpd | mg/L | F | South | North | DO | kwh | gpd | gpd | gpd | gpd | %sol | #/DT | [8 empty] | mcf/d | South | North | South | North | 1000cuft/d | Low Level | %sol | %vol | %sol | %vol | South | North | South | North | inf | eff | inf | eff | gpd | mg/L | F | High level | South | North | DO | kwh | gpd | gpd | gpd | gpd | %sol | #/DT | [21 empty] | 9 | 579328
2016-02-24 | 2016-02-24 | 91 | 3.3834 | 5.1047 | 1.3333 | 0.96552 | 66.2 |  |  | 3.98 | 81 | 2.04 | 63.5 | 2800 | 2800 | 4500 | 4100 | 16.7 | 10.2 | 28969.824 | 17694.144 | 2150 | 0.47 | 102 | 8.9 | 5.5 | 6.82 | 52.8719 | 0 | 0 | 0 | 0 | [8 empty] | 4 | 1: 2016-02-24 | [16 empty] | 10 | 497874
2016-02-25 | 2016-02-25 | 90 | 5.4313 | 13.8052 | 1.2381 | 0.89655 | 43.9 |  |  | 4.07 | 77.7 | 1.78 | 67.1 | 2600 | 2600 | 5000 | 5600 | 29.4 | 10.2 | 25009.992 | 8676.936 | 970 | 0.5 | 105 | 22.2* | 16.8* | 6.9425 | 51.2902 | 0 | 0 | 0 | 1903.5 | [8 empty] | 5 | 1: 2016-02-25 | [16 empty] | 11 | 571251
2016-02-26 | 2016-02-26 | 91.5 | 5.6162 | 12.7123 |  |  | 33.2 | [10 empty] | 40.3 | 15.3 | 28904.772 | 10973.772 | 590 | 0.43 | 105 | 16.1* | 14 | 4.695 | 51.4083 | 0 | 0 | 0 | 2115 | [8 empty] | 6 | 1: 2016-02-26 | [16 empty] | 12 | 470264
2016-02-27 | 2016-02-27 | 91.5 | 5.5192 | 12.8541 |  |  | 23.1 | [10 empty] | 39 | 16.5 | 29273.4 | 12384.9 | 730 | 0.4 | 105 | 15.3 | 13.4 | 3.9225 | 50.6769 | 0 | 0 | 0 | 1621.5 | [8 empty] | 7 | 1: 2016-02-27 | [16 empty] | 13 | 581599
2016-02-28 | 2016-02-28 | 88.6 | 3.7269 | 10.8431 | 1.1818 | 1.0303 | 69.7 | [6 empty] | 2600 | 3400 | 2400 | 3500 | 39.3 | 18.2 | 29826.342 | 13812.708 | 530 | 0.46 | 105 | 8.7 | 11.5 | 3.9225 | 53.04 | 0 | 0 | 0 | 2467.5 | [8 empty] | 1 | 1: 2016-02-28 | [16 empty] | 14 | 405522
2016-02-29 | 2016-02-29 | 86.5 | 5.4569 | 13.9368 | 1.2 | 0.45833 | 62.2 |  |  | 3.59 | 78.9 | 2 | 64 | 2400 | 3300 | 4100 | 4000 | 38 | 16.7 | 29156.64 | 12813.576 | 630 | 0.43 | 104 | 12.3 | 13.3 | 3.6175 | 57.1279 | 0 | 0 | 0 | 1904 | [8 empty] | 2 | 1: 2016-02-29 | [16 empty] | 15 | 431525
2016-03-01 | 2016-03-01 | 93.8 | 5.3391 | 15.0* | 1.7857 | 1.0645 | 72 | 96 | 155 | 3.8 | 79.7 | 2.1 | 69.2 | 5000 | 3300 | 4800 | 4700 | 37.6 | 15.7 | 29476.896 | 12308.172 | 690 | 0.44 | 103 | 23.2* | 15.8* | 4.13 | 53.8042 | 0 | 0 | 0 | 423 | [8 empty] | 3 | 1: 2016-03-01 | [16 empty] | 16 | 415235
2016-03-02 | 2016-03-02 | 99.6 | 3.1814 | 4.2823 | 1.1667 | 0.75 | 65.7 |  |  | 3.4 | 81.2 | 2.5 | 71 | 2100 | 2100 | 3700 | 3500 | 31.8 | 19.8 | 25990.776 | 16182.936 | 1650 | 0.43 | 103 | 10.2 | 11.3 | 4.6225 | 57.204 | 0 | 0 | 0 | 0 | [8 empty] | 4 | 1: 2016-03-02 | [16 empty] | 17 | 483354
2016-03-03 | 2016-03-03 | 101.4 | 7.3342 | 10.5568 | 1.08 | 0.64583 | 63.1 |  |  | 3.46 | 82 | 2 | 68 | 2700 | 3100 | 5100 | 3900 | 38.8 | 15.9 | 26534.544 | 10873.692 | 1070 | 0.6 | 104 | 26.1* | 10.8 | 4.145 | 57.4361 | 0 | 0 | 0 | 0 | [8 empty] | 5 | 1: 2016-03-03 | [16 empty] | 18 | 507946
2016-03-04 | 2016-03-04 | 101.2 | 5.1953 | 9.1427 |  |  | 49.9 | [10 empty] | 35.8 | 14.8 | 28662.912 | 11849.472 | 830 | 0.45 | 104 | 13.1 | 11.7 | 4.1575 | 56.316 | 0 | 0 | 0 | 1198.5 |  | 0 | [6 empty] | 6 | 1: 2016-03-04 | [16 empty] | 19 | 549171
2016-03-05 | 2016-03-05 | 99.2 | 5.2209 | 10.5385 |  |  | 49.2 | [10 empty] | 39 | 14.5 | 27972.36 | 10399.98 | 1020 | 0.45 | 104 | 14.6 | 13 | 4.965 | 56.328 | 0 | 0 | 0 | 2397 | [8 empty] | 7 | 2016-03-05 | 95.8 | 5.1 | 9.9 | 1.3 | 0.8 | 61.7 | 160 | 3.6 | 80.5 | 2.2 | 68.1 | 2960 | 3040 | 4020 | 3920 | 37.2 | 16.5 | 28231.5 | 12605.8 | 917 | 0.47 | 103.9 | 96 | 11.8 | 11.9 | 4.2 | 55.9 | 0 | 0 | 0 | 1200 | #DIV/0! | 0 | [21 empty] | 20 | 298104
2016-03-06 | 2016-03-06 | 100.2 | 5.0036 | 19.9* | 0.68571 | 0.6087 | 64.7 | [6 empty] | 2400 | 2800 | 3500 | 6500 | 39.3 | 14.3 | 28187.532 | 10256.532 | 880 | 0.46 | 105 | 23.9* | 21.7* | 4.2325 | 56.124 | 0 | 0 | 0 | 1621.5 | [8 empty] | 1 | 1: 2016-03-06 | [16 empty] | 21 | 570650
2016-03-07 | 2016-03-07 | 101.1 | 5.7071 | 10.4321 | 1.3158 | 0.63636 | 48.7 |  |  | 3.23 | 83.5 | 1.81 | 67.4 | 2500 | 2800 | 4000 | 3700 | 36.9 | 15 | 25850.664 | 10508.4 | 1170 | 0.46 | 105 | 16.4* | 13.1 | 3.9275 | 56.3801 | 0 | 0 | 0 | 2608.5 | [8 empty] | 2 | 1: 2016-03-07 | [16 empty] | 22 | 569351
2016-03-08 | 2016-03-08 | 98.1 | 3.7686 | 10.1431 | 1.5909 | 0.6875 | 70.1 | 137 | 337 | 4.16 | 85.6 | 1.92 | 68 | 3500 | 2200 | 3600 | 3900 | 40.3 | 16.7 | 29240.874 | 12117.186 | 970 | 0.6 | 106 | 9.8 | 13 | 3.5925 | 56.4158 | 0 | 0 | 0 | 415 | [8 empty] | 3 | 1: 2016-03-08 | [16 empty] | 23 | 505115
2016-03-09 | 2016-03-09 | 98.1 | 5.7536 | 10.4358 | 1.4706 | 0.66667 | 72.4 |  |  | 3.5 | 83.3 | 2 | 68.5 | 2500 | 3200 | 4400 | 4600 | 39.6 | 14.2 | 30384.288 | 10895.376 | 690 | 0.42 | 107 | 12.9 | 16.2* | 4.3175 | 54.372 | 0 | 0 | 0 | 2679 | [8 empty] | 4 | 1: 2016-03-09 | [16 empty] | 24 | 271694
2016-03-10 | 2016-03-10 | 95.6 | 6.8714 | 10.5435 | 1.069 | 0.83333 | 66.8 |  |  | 3.4 | 81.4 | 1.99 | 68 | 3100 | 3500 | 5200 | 4900 | 37.8 | 13.8 | 28372.68 | 10358.28 | 930 | 0.41 | 108 | 19.9* | 11.6 | 4.0125 | 55.6121 | 0 | 0 | 0 | 1904 | [8 empty] | 5 | 1: 2016-03-10 | [16 empty] | 25 | 1076498
2016-03-11 | 2016-03-11 | 100.8 | 5.241 | 8.398 |  |  | 56.8 | [10 empty] | 38.8 | 14 | 28476.096 | 10274.88 | 970 | 0.45 | 108 | 14.2 | 12.7 | 3.965 | 57.5119 | 0 | 0 | 0 | 2820 | [8 empty] | 6 | 1: 2016-03-11 | [16 empty] | 26 | 1144233
2016-03-12 | 2016-03-12 | 97.7 | 5.2433 | 10.5372 |  |  | 46 | [10 empty] | 38.9 | 13.3 | 28225.062 | 9650.214 | 880 | 0.45 | 104 | 14.4 | 12.9 | 3.9175 | 56.2159 | 0 | 0 | 0 | 1974 | [8 empty] | 7 | 2016-03-12 | 98.8 | 5.4 | 10.1 | 1.2 | 0.7 | 60.8 | 340 | 3.6 | 83.5 | 1.9 | 68 | 2800 | 2900 | 4140 | 4720 | 38.8 | 14.5 | 28391 | 10580.1 | 927 | 0.46 | 106.1 | 137 | 12.8 | 12.7 | 4 | 56.1 | 0 | 0 | 0 | 2000 | #DIV/0! | #DIV/0! | [21 empty] | 27 | 1000754
2016-03-13 | 2016-03-13 | 98.8 | 2.8795 | 6.6115 | 1.2381 | 0.77143 | 43.9 | [6 empty] | 2600 | 2700 | 2300 | 2600 | 41.9 | 13.8 | 30401.802 | 10013.004 | 870 | 0.44 | 107 | 6.4 | 9.2 | 4.025 | 56.3719 | 0 | 0 | 0 | 0 | [8 empty] | 1 | 1: 2016-03-13 | [16 empty] | 28 | 226626
2016-03-14 | 2016-03-14 | 101.2 | 4.3752 | 7.7337 | 1.4706 | 0.90625 | 86.3 |  |  | 2.9 | 85.8 | 1.5 | 68.3 | 2500 | 2900 | 4000 | 3900 | 29.2 | 14.7 | 33119.808 | 16673.328 | 1950 | 0.51 | 104 | 9.6 | 7.3 | 3.8725 | 56.6921 | 0 | 0 | 0 | 2472.5 | [8 empty] | 2 | 1: 2016-03-14 | [16 empty] | 29 | 237990
2016-03-15 | 2016-03-15 | 95.4 | 5.1633 | 7.3611 | 1.9286 | 0.96 | 59.2 | 1520 | 1190 | 3.5 | 82.4 | 1.8 | 68.2 | 2700 | 2400 | 4200 | 4100 | 33.3 | 13.7 | 26661.312 | 10968.768 | 1070 | 0.45 | 102 | 8.3 | 11 | 4.96 | 55.0399 | 0 | 0 | 0 | 2533 | [8 empty] | 3 | 1: 2016-03-15 | [16 empty] | 30 | 139466
2016-03-16 | 2016-03-16 | 96.3 | 4.1339 | 8.7113 | 1.5263 | 0.96552 | 81.9 |  |  | 3.91 | 74.5 | 1.8 | 64.4 | 2900 | 2800 | 3700 | 4200 | 36.5 | 13.2 | 26179.26 | 9467.568 | 1120 | 0.46 | 100 | 13.2 | 16.3* | 3.9975 | 54.3641 | 0 | 0 | 0 | 563.5 | [8 empty] | 4 | 1: 2016-03-16 | [16 empty] | 31 | 251722
2016-03-17 | 2016-03-17 | 93.5 | 5.7544 | 9.641 | 1.3043 | 0.91429 | 62.4 |  |  | 3.64 | 79.8 | 1.75 | 67.4 | 3000 | 3200 | 4500 | 4400 | 38.3 | 12.7 | 27789.714 | 9214.866 | 1380 | 0.46 | 102 | 15.9* | 11.2 | 3.685 | 52.2079 | 0 | 0 | 0 | 2185.5 | [8 empty] | 5 | 1: 2016-03-17 | [16 empty] | Total | 14089071
2016-03-18 | 2016-03-18 | 95.9 | 5.2747 | 8.4096 |  |  | 42.5 | [10 empty] | 38.8 | 13.1 | 27181.728 | 9177.336 | 770 | 0.47 | 96 | 14.9 | 13.3 | 3.7025 | 54.5122 | 0 | 0 | 0 | 2185.5 | [8 empty] | 6 | 1: 2016-03-18
2016-03-19 | 2016-03-19 | 100.4 | 5.294 | 8.4589 |  |  | 51.6 | [10 empty] | 41.2 | 12.8 | 29893.896 | 9287.424 | 1170 | 0.45 | 96 | 14.4 | 12.9 | 3.6425 | 55.1839 | 0 | 0 | 0 | 846 | [8 empty] | 7 | 2016-03-19 | 97.4 | 4.7 | 8.1 | 1.5 | 0.9 | 61.1 | 1190 | 3.5 | 80.6 | 1.7 | 67.1 | 2740 | 2800 | 3740 | 3840 | 37 | 13.4 | 28746.8 | 10686 | 1190 | 0.46 | 101 | 1520 | 11.1 | 10.8 | 4 | 54.9 | 0 | 0 | 0 | 1540 | #DIV/0! | #DIV/0!
2016-03-20 | 2016-03-20 | 98.8 | 11.5* | 182.9* | 1.35 | 0.81579 | 49.9 | [6 empty] | 2700 | 3100 | 4200 | 6100 | 39.5 | 13.6 | 30966.42 | 10661.856 | 1020 | 0.4 | 97 | 12.4 | 16.0* | 3.1975 | 55.7239 | 0 | 0 | 0 | 2256 | [8 empty] | 1 | 1: 2016-03-20
2016-03-21 | 2016-03-21 | 98.8 | 4.7806 | 106.3* | 1.0645 | 0.925 | 104.2 |  |  | 2.73 | 82.5 | 1.92 | 68.8 | 3300 | 3700 | 4500 | 4700 | 37.4 | 12.9 | 31191.6 | 10758.6 | 1070 | 0.46 | 98 | 13.4 | 16.2* | 3.665 | 54.7639 | 0 | 0 | 0 | 2890.5 | [8 empty] | 2 | 1: 2016-03-21
2016-03-22 | 2016-03-22 | 98.8 | 6.3 | 9.0462 | 1.3 | 0.75556 | 91.7 | 111 | 224 | 2.78 | 84.3 | 1.9 | 67.3 | 3900 | 3400 | 4900 | 4300 | 40.5 | 12.3 | 31412.61 | 9540.126 | 780 | 0.45 | 99 | 14.6 | 11.9 | 3.6675 | 54.6202 | 0 | 0 | 0 | 1692 | [8 empty] | 3 | 1: 2016-03-22
2016-03-23 | 2016-03-23 | 96.5 | 5.2534 | 8.8481 | 1 | 1.2222 | 59.4 |  |  | 2.98 | 81.8 | 1.68 | 68.2 | 3300 | 3300 | 5300 | 4500 | 39.2 | 12 | 30404.304 | 9307.44 | 1660 | 0.5 | 101 | 12.7 | 13.4 | 2.815 | 54.912 | 0 | 0 | 0 | 1974 | [8 empty] | 4 | 1: 2016-03-23
2016-03-24 | 2016-03-24 | 93.5 | 5.6391 | 7.2101 | 1.037 | 0.67391 | 44.7 |  |  | 3.06 | 82.9 | 2.02 | 69.9 | 2800 | 3100 | 4000 | 3700 | 39.8 | 11.6 | 27882.288 | 8126.496 | 1220 | 0.44 | 100 | 13.2 | 13.1 | 3.9325 | 56.88 | 0 | 0 | 0 | 705 | [8 empty] | 5 | 1: 2016-03-24
2016-03-25 | 2016-03-25 | 90.7 | 5.2235 | 7.8311 |  |  | 51.6 | [10 empty] | 39.6 | 12.3 | 28072.44 | 8719.47 | 1270 | 0.44 | 104 | 14.7 | 13.2 | 3.59 | 55.0402 | 0 | 0 | 0 | 2467.5 | [8 empty] | 6 | 1: 2016-03-25
2016-03-26 | 2016-03-26 | 92.5 | 5.2287 | 7.7777 |  |  | 64.5 | [10 empty] | 40.7 | 13.3 | 28173.354 | 9206.526 | 1120 | 0.46 | 104 | 15.1 | 13.5 | 3.3475 | 55.884 | 0 | 0 | 0 | 2608.5 | [8 empty] | 7 | 2016-03-26 | 95.7 | 5.4 | 8.1 | 1.2 | 0.9 | 66.6 | 220 | 2.9 | 82.9 | 1.9 | 68.6 | 3200 | 3320 | 4580 | 4660 | 39.5 | 12.6 | 29729 | 9474.4 | 1163 | 0.45 | 100.4 | 111 | 13.7 | 13 | 3.5 | 55.4 | 0 | 0 | 0 | 2080 | #DIV/0! | #DIV/0!
2016-03-27 | 2016-03-27 | 94.6 | 3.5566 | 5.8726 | 0.56522 | 0.49206 | 87 | [6 empty] | 2600 | 3100 | 2900 | 3100 | 39.1 | 11.5 | 27717.99 | 8152.35 | 1220 | 0.44 | 103 | 10.2 | 9.3 | 3.695 | 55.5761 | 0 | 0 | 0 | 1974 | [8 empty] | 1 | 1: 2016-03-27
2016-03-28 | 2016-03-28 | 92.9 | 4.4766 | 5.3218 | 0.73333 | 0.79412 | 41.4 |  |  | 3.08 | 82.1 | 1.9 | 71.4 | 3300 | 2700 | 4500 | 3400 | 27.5 | 12.8 | 30044.85 | 13984.512 | 2330 | 0.47 | 100 | 12.6 | 4.5 | 3.7975 | 54.7039 | 0 | 0 | 0 | 1692 | [8 empty] | 2 | 1: 2016-03-28
2016-03-29 | 2016-03-29 | 88.4 | 5.8821 | 8.0139 | 0.64151 | 0.69767 | 71.5 | 98 | 225 | 3.55 | 83 | 1.35 | 72.2 | 3400 | 3000 | 4800 | 4500 | 39.5 | 11 | 27013.26 | 7522.68 | 1080 | 0.43 | 102 | 16.6* | 13 | 3.89 | 55.6481 | 0 | 0 | 0 | 0 | [8 empty] | 3 | 1: 2016-03-29
2016-03-30 | 2016-03-30 | 93.5 | 5.1231 | 6.7444 | 0.75 | 0.8 | 128 |  |  | 3.6 | 80.6 | 1.55 | 69.2 | 3600 | 3200 | 4500 | 4000 | 39.5 | 11.4 | 27342.69 | 7891.308 | 1610 | 0.43 | 103 | 19.2* | 13.3 | 3.615 | 56.0801 | 0 | 0 | 0 | 423 | [8 empty] | 4 | 1: 2016-03-30
2016-03-31 | 2016-03-31 | 88.8 | 5.5545 | 8.3003 | 0.90244 | 0.94118 | 90.4 |  |  | 2.97 | 83.1 | 1.89 | 77.6 | 3700 | 3200 | 4500 | 4200 | 37.9 | 11.4 | 25919.052 | 7796.232 | 1260 | 0.42 | 103 | 24.9* | 15.3* | 3.5075 | 54.9161 | 0 | 0 | 0 | 1833 | [8 empty] | 5 | 1: 2016-03-31
| Avg | 96.6 | 5.1 | 8.4 | 1.2 | 0.8 | 65.7 | 390 | 430 | 3.4 | 82.1 | 1.9 | 69.1 | 3050 | 2990 | 4220 | 4230 | 37.9 | 13.6 | 28540.1 | 10391.8 | 1152 | 0.5 | 103 | 12.5 | 11.7 | 3.9 | 55.6 | 0 | 0 | 0 | 1591.7 | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Formulas:
SRT = IF(DMREZ!D11>TODAY()-2,"",((IF(ISNUMBER([Average Aerator]),[Average Aerator],O42)*2.52*[AER.])/(([Plant Flows (MGD)]*IF(ISNUMBER([Plant]),[Plant],K42)*(+[AER.]/([AER.]+[AER.])))+(HQ14*IF(ISNUMBER(AT_!Q11),AT_!Q11,AT_!$Q42)))))
North = IF(DMREZ!D12>TODAY()-2,"",((IF(ISNUMBER([North]),[North],P42)*2.52*[AER.])/(([Plant Flows (MGD)]*IF(ISNUMBER([Plant]),[Plant],K42)*([AER.]/([AER.]+[AER.]))+((PT_!BN12+2.5/3.5*PT_!BP12)*IF(ISNUMBER(AT_!S12),AT_!S12,AT_!$S42))))))
Previous Month Update the links = +[D]
D = +[D, row below]-1
sludge prd = IF([D]>TODAY()-2,"",+AT_!DJ11)

## CLA_
| #DIV/0! |  | 1 | [20 empty] | 1
| 192.0829 |  | 199.26 |  | 110 | 110 | 40 | 2690 | 4450 | 3440 | 4580 | 4010 | 3620 | 5430 | 5980 | 5690 | 6540 | 5580 | 9020 |  | 7290 |  | 192.2267 | 196.3048 | 122.5295 | 123 | 12.6228 | 5602.1484 | 4 |  |  | 71.7096 |  |  | #DIV/0! | [30 empty] | 39.86 | 2.57 | 4.46 | 363 | [27 empty] | #DIV/0! |  |  |  | #DIV/0!
| 104.6268 |  | 101.7722 |  | 40 | 60 | -10 | -1330 | 1580 | 2090 | 1730 | 2250 | 2080 | 2930 | 2670 | 2640 | 2170 | 2630 | 4490 |  | 3580 |  | 89.7088 | 100.3404 | 52.2074 | 50 | -1.2035 | 75.7464 | 3 |  |  | 66.5009 |  |  | #DIV/0! | [30 empty] | 33.3787 | 2.2 | 3.84 | 333 | [27 empty] | #DIV/0! |  |  |  | #DIV/0!
| MONTH: |  | 2016-03-01 |  | 2016
| Total Suspended Solids (mg/L) | [21 empty] | Carb. Biochemical Oxygen Demand (mg/L) | [15 empty] | Digester Control | [14 empty] | Chlorides Influent |  | Plant Influent (mg/L) | [13 empty] | Primary Effluent | [6 empty] | Plant Effluent | [6 empty] | Waste Sludge |  |  |  | Waste Sludge |  |  |  | Dewatering Nutrient Analysis | [17 empty] | Dewatering Solids Analysis
D | Raw Sewage |  |  |  | Prim Eff | Prim Eff | Plant | Thick | Aerator Effluent |  |  |  |  | Average Aerator |  |  |  |  | Return Sludge |  | Return Sludge |  | Raw |  | Primary |  | Plant | Thickener | Thickened |  | Primary Digester |  | Secondary Digester |  | Waste Sludge |  |  |  | Digester Volatiles |  |  |  |  | Alkalinity |  |  |  |  | pH |  |  |  |  | (mg/L) |  | High Level | [6 empty] | Lower Level | [6 empty] | (mg/L) | [6 empty] | (mg/L) | [6 empty] | North |  |  |  | South |  |  |  | Treated Centrate (SCT) | [7 empty] | Centrate (mg/L) |  |  |  | Cake (mg/L) | [7 empty] | Cake |  | Centrate |  | Centrate |  |  |  | D | Special Centrate Sample
A | High Level |  | Lower Level |  | South | North | Eff | Eff | (mg/L) |  |  |  |  | (mg/L) |  |  |  |  | South |  | North |  | Sewage |  | Effluent |  |  | Feed | Sludge |  | Sludge |  | Sludge |  | South |  | North |  | (mg/L) |  |  |  |  | (mg/L) | [9 empty] | High | Lower | Nitrogen |  |  |  | Phosphorus |  | Demand | Nitrogen |  |  |  | Phosphorus |  | Demand | Nitrogen |  |  |  | Phosphorus |  | Demand | Nitrogen |  |  |  | Phosphorus |  | Demand | (mg/L) |  |  |  | (mg/L) |  |  |  | Nitrogen |  |  | Alkalinity | TSS (mg/L) | pH |  |  | pH | Nitrogen |  | Phosphorus | PH | Nitrogen |  |  |  | Phosphorus | Sludge Feed |  |  |  | %SOL | %VOL | SS | VOL. SS | CBOD | ALK | A | CBOD | TSS | TVS | Sample
Y | Total | %VOL | Total | %VOL | (mg/L) | (mg/L) | (mg/L) | (mg/L) | NO.1&2 | NO.3&4 | NO.5&6 | NO.7&8 | NO.9&10 | NO.1&2 | NO.3&4 | NO.5&6 | NO.7&8 | NO.9&10 | Total | %VOL | Total | %VOL | H.L. | L.L. | South | North | Effluent | TSS (mg/L) | %SOL | %VOL | %SOL | %VOL | %SOL | %VOL | %SOL | %VOL | %SOL | %VOL | No. 3 | No. 5 | No. 6 | No.7 | No.8 | No. 3 | No. 5 | No. 6 | No.7 | No.8 | No. 3 | No. 5 | No. 6 | No.7 | No.8 | Level | Level | NO2 | NO3 | NH3 (NH3) | TKN | Ortho | Total | COD | NO2 | NO3 | NH3 (NH3) | TKN | Ortho | Total | COD | NO2 | NO3 | NH3 | TKN | Ortho | Total | COD | NO2 | NO3 | NH3 (NH3) | TKN | Ortho | Total | COD | NO2 | NO3 | NH3 | TKN | NO2 | NO3 | NH3 | TKN | NO2 | NO3 | NH3 | [6 empty] | NH3 | Alk | Total |  | NO2 | NO3 | NH3 | TKN | Total | %SOL | %VOL | %SOL | %VOL | Total |  | (mg/L) | % | (mg/L) | (mg/L) | Y | (mg/L) |  |  | Receipt
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 103 | 104 | 105 | 106 | 107 | 108 | 109 | 110 | 111 | 112 | 113 | 114 | 115 | 116 | 117 | 118 | 119 |  |  |  |  | 1
1 | 119 |  | 120 |  | 50 | 72 | 7 | 160 | 5380* | 6100* | 4970 | 3720 | 2860 | 4310 | 4740 | 5230 | 4740 | 4670 | 7680 |  | 5080 |  | 138 | 162 | 90 | 89 | 5 | 2060 | 3.8 | 79.7 | 2.1 | 69.2 | [21 empty] | 96 | 155 | 0.04 | 0.16 | 27.56 | 37.4 | 2.67 | 4.59 | 373 | 0.04 | 0.12 | 27.7 | 37.4 | 2.57 | 4.46 | 363 | 0 | 0.02 | 22.5 | 31.3 | 2.56 | 4.72 | 233 | 0.83 | 2.8 | 11.8 | 12.1 | 1.27 | 1.49 | 47
2 | 136 | 78 | 112 | 80.4 | 84 | 72 | 72 | 176 | 2030 | 2190 | 2050 | 2220 | 2020 | 3550 | 3840 | 3730 | 3500 | 3430 | 7520 | 80.3 | 7860 | 78.4 | 140 | 133 | 68 | 63 | 21 | 2240 | 3.4 | 81.2 | 2.5 | 71 | [23 empty] | 0.12 | 0.24 | 21.86 | 31.7 |  |  |  | 0.11 | 0.24 | 22.7 | 31 | [10 empty] | 0.86 | 2.73 | 11.3 | 16.2
3 | 124 |  | 151 |  | 54 | 100 | 20 | 96 | 5090* | 2710 | 5110* | 3110 | 3040 | 4630 | 5630 | 5120 | 3970 | 3890 | 5500 |  | 4650 |  | 171 | 191 | 98 | 132 | 8 | 940 | 3.46 | 82 | 2 | 68 | [6 empty] | 190 |  | 140 | 450 | 180 | 3500 |  | 3800 | 3200 | 3000 | 7.1 |  | 7.2 | 6.9 | 7.1 |  |  | 0.13 | 0.14 | 28.9 | 38.7 |  |  |  | 0.11 | 0.1 | 28.3 | 38.3 | [10 empty] | 1.06 | 3.09 | 10.8 | 11.7
4 | 120 |  | 130 |  |  |  | 9 | [15 empty] | 124 | 111 |  |  | 4 | [28 empty] | 0.11 | 0.12 | 27.81 | 35.5 |  |  |  | 0.1 | 0.11 | 26.7 | 35.8 | [10 empty] | 1.03 | 2.48 | 10.7 | 11.3
5 | 142 |  | 106 |  |  |  | 9 | [15 empty] | 165 | 154 |  |  | 6 | [28 empty] | 0.05 | 0.07 | 30.96 | 39.4 |  |  |  | 0.06 | 0.07 | 30.7 | 38 | [10 empty] | 1.2 | 2.68 | 9.7 | 10.6
6 | 142 |  | 136 |  | 64 | 79 | 10 |  | 2360 | 2250 | 2720 | 3020 | 2600 | 10450* | 3730 | 3330 | 6410 | 6580 | 5840 |  | 4740 |  | 160 | 160 |  |  | 6 | [28 empty] | 0.05 | 0.12 | 30.84 | 39.8 |  |  |  | 0.09 | 0.04 | 30.6 | 38 | [10 empty] | 1.11 | 2.08 | 9.6 | 11.1
7 | 146 | 78.1 | 142 | 77.5 | 66 | 76 | 10 | 150 | 2350 | 2550 | 2490 | 2450 | 3150 | 3660 | 4090 | 4290 | 3680 | 3760 | 5860 | 80.9 | 5080 | 79.9 | 107 | 111 | 81 | 82 | 5 | 640 | 3.23 | 83.5 | 1.81 | 67.4 | [6 empty] | 170 |  | 180 | 130 | 130 | 3600 |  | 3800 | 2000 | 3800 | 7.29 |  | 7.36 | 7.12 | 7.2 |  |  | 0.14 | 0 | 27.69 | 36.9 |  |  |  | 0.15 | 0 | 26.5 | 36.6 | [10 empty] | 1.2 | 1.47 | 11.7 | 12.3
8 | 176 |  | 168 |  | 96 | 78 | 11 | 160 | 3590 | 3270 | 3540 | 2440 | 2030 | 3360 | 3710 | 3580 | 3970 | 3790 | 8060 |  | 5500 |  | 106 | 142 | 106 | 77 | 7 | 960 | 4.16 | 85.6 | 1.92 | 68 | [21 empty] | 137 | 337 | 0.11 | 0.03 | 30.96 | 41.4 |  |  |  | 0.11 | 0 | 29.1 | 37.9 |  |  |  | 0.07 | 0 | 25.7 |  |  |  |  | 1.05 | 2.28 | 13.4 | 13.4
9 | 164 | 82.9 | 168 | 81 | 84 | 70 | 7 | 210 | 2460 | 2470 | 2490 | 3500 | 2900 | 4220 | 4620 | 4380 | 4720 | 4550 | 6500 | 78.2 | 6660 | 77.5 | 148 | 157 | 81 | 82 | 4 | 1760 | 3.5 | 83.3 | 2 | 68.5 | [23 empty] | 0.04 | 0.09 | 28.9 | 39.4 |  |  |  | 0.04 | 0.07 | 28.9 | 39.7 | [10 empty] | 0.97 | 2.76 | 10 | 10.5
10 | 152 |  | 158 |  | 66 | 106 | 8 | 120 | 5530* | 2780 | 3350 | 3560 | 3470 | 4890 | 5300 | 5340 | 5780 | 4090 | 6400 |  | 6400 |  | 175 | 181 | 97 | 108 | 6 | 1980 | 3.4 | 81.4 | 1.99 | 68 | [6 empty] | 220 |  | 200 | 190 | 160 | 3100 |  | 3200 | 3100 | 3100 | 7.1 |  | 7.1 | 7.1 | 7.1 |  |  | 0.13 | 0 | 27.32 | 37.8 |  |  |  | 0.12 | 0 | 27 | 37.5 | [10 empty] | 1.2 | 2.7 | 8.6 | 9.9
11 | 152 |  | 140 |  |  |  | 8 | [15 empty] | 145 | 153 |  |  | 7 | [28 empty] | 0.11 | 0 | 30.48 | 39.9 |  |  |  | 0.11 | 0 | 28.7 | 36.4 | [10 empty] | 1.43 | 2.24 | 9 | 10.3
12 | 170 |  | 148 |  |  |  | 8 | [15 empty] | 140 | 137 |  |  | 5 | [28 empty] | 0.12 | 0.03 | 30.6 | 39.1 |  |  |  | 0.12 | 0 | 30.7 | 38.1 | [10 empty] | 1.45 | 1.73 | 9 | 10.1
13 | 180 |  | 184 |  | 94 | 74 | 8 |  | 2510 | 2450 | 2830 | 2640 | 2720 | 2440 | 2470 | 2110 | 2550 | 2660 | 6780 |  | 5560 |  | 155 | 154 |  |  | 5 | [28 empty] | 0.05 | 0.08 | 31.21 | 43 |  |  |  | 0.05 | 0.05 | 31 | 39.6 | [10 empty] | 1.27 | 3.04 | 7.9 | 9.5
14 | 224 | 78.6 | 220 | 81.8 | 70 | 90 | 24 | 220 | 2440 | 2480 | 2640 | 3150 | 2590 | 4370 | 3720 | 3800 | 3760 | 3950 | 1760* | 80.7 | 4840 | 84.3 | 89 | 95 | 77 | 92 | 11 | 4540 | 2.9 | 85.8 | 1.5 | 68.3 | [6 empty] | 170 |  | 380 | 190 | 320 | 3100 |  | 3500 | 3100 | 3600 | 6.98 |  | 7.1 | 6.99 | 7.06 |  |  | 0.07 | 0.42 | 18.21 | 29.5 |  |  |  | 0.09 | 0.35 | 17.6 | 27.4 | [10 empty] | 0.86 | 1.84 | 8.7 | 12
15 | 156 |  | 162 |  | 120 | 88 | 15 | 330 | 2660 | 2650 | 2720 | 2550 | 2290 | 4090 | 4310 | 4070 | 4290 | 3920 | 6620 |  | 6660 |  | 108 | 152 | 54 | 66 | 6 | 3220 | 3.5 | 82.4 | 1.8 | 68.2 | [21 empty] | 1520 | 1190 | 0.21 | 0.01 | 20.76 | 33.2 | 2.23 | 4.04 | 375 | 0.2 | 0.06 | 20.8 | 32.8 | 2.2 | 3.84 | 333 | 0.18 | 0.09 | 17.4 | 24.4 | 2.12 | 4.01 | 213 | 1.39 | 2.54 | 7 | 9.8 | 3.32 | 6.45 | 84
16 | 144 | 86.1 | 162 | 82.7 | 74 | 68 | 6 | 880 | 3280 | 2930 | 2530 | 2790 | 2780 | 3990 | 3830 | 3270 | 3950 | 4360 | 7700 | 78.2 | 6840 | 78.7 | 129 | 146 | 85 | 68 | 3 | 3680 | 3.91 | 74.5 | 1.8 | 64.4 | [23 empty] | 0.07 | 0.09 | 28.66 | 37.23 |  |  |  | 0.15 | 0 | 25.6 | 34.7 | [10 empty] | 1.5 | 3.11 | 8 | 8.6
17 | 182 |  | 156 |  | 74 | 102 | 6 | 160 | 3100 | 2980 | 2940 | 3280 | 3100 | 4370 | 5010 | 4080 | 4230 | 4560 | 6700 |  | 5600 |  | 143 | 142 | 82 | 115 | 3 | 2530 | 3.64 | 79.8 | 1.75 | 67.4 | [6 empty] | 210 |  | 440 | 200 | 370 | 3500 |  | 3400 | 2900 | 3500 | 7.2 |  | 7.01 | 7.14 | 7.1 |  |  | 0.02 | 0.12 | 29.87 | 39.2 |  |  |  | 0.02 | 0.09 | 31.8 | 36.2 | [10 empty] | 1.12 | 2.97 | 7.7 | 8.6
18 | 140 |  | 131 |  |  |  | 7 | [15 empty] | 140 | 152 |  |  | 3 | [28 empty] | 0.02 | 0.11 | 28.78 | 39.6 |  |  |  | 0.02 | 0.08 | 28.2 | 37 | [10 empty] | 1.24 | 3.39 | 7.7 | 8.5
19 | 131 |  | 146 |  |  |  | 6 | [15 empty] | 146 | 166 |  |  | 4 | [28 empty] | 0 | 0.12 | 32.06 | 41.8 |  |  |  | 0 | 0.09 | 30.7 | 39.9 | [10 empty] | 1.1 | 2.89 | 8.2 | 8.8
20 | 128 |  | 132 |  | 82 | 92 | 8 |  | 2590 | 2400 | 3080 | 3250 | 2870 | 4840 | 4000 | 3750 | 7820 | 4420 | 2940 |  | 5480 |  | 183 | 180 |  |  | 4 | [28 empty] | 0 | 0.11 | 31.69 | 40.5 |  |  |  | 0 | 0.09 | 30.1 | 37.3 | [10 empty] | 1.09 | 2.45 | 9.3 | 10.1
21 | 138 | 84.1 | 156 | 84.6 | 224* | 66 | 10 | 400 | 4510* | 3260 | 5170* | 3770 | 3620 | 4120 | 4990 | 4520 | 5140 | 4200 | 7920 | 82.6 | 3820 | 84.3 | 120 | 131 | 124 | 64 | 6 | 2840 | 2.73 | 82.5 | 1.92 | 68.8 | [6 empty] | 250 |  | 420 | 150 | 220 | 3100 |  | 3000 | 2900 | 3000 | 7 |  | 7 | 7 | 7 |  |  | 0.02 | 0.13 | 28.66 | 38.8 |  |  |  | 0.03 | 0.1 | 26.6 | 34.4 | [10 empty] | 1 | 1.85 | 9.4 | 10
22 | 138 |  | 150 |  | 82 | 88 | 9 | 142 | 4440 | 2900 | 4460 | 3470 | 3310 | 5190 | 4660 | 4720 | 4320 | 4330 | 6540 |  | 5000 |  | 161 | 174 | 82 | 96 | 5 | 3360 | 2.78 | 84.3 | 1.9 | 67.3 | [21 empty] | 111 | 224 | 0 | 0.13 | 32.3 | 40.9 |  |  |  | 0.01 | 0.1 | 30.8 | 39.3 |  |  |  | 0 | 0.05 | 24 |  |  |  |  | 1.34 | 2.52 | 7 | 8.4
23 | 164 | 86.6 | 162 | 84 | 102 | 82 | 9 | 360 | 5530* | 3300 | 6600* | 3530 | 2970 | 4960 | 5540 | 5270 | 4640 | 4270 | 8580 | 80 | 5680 | 79.2 | 162 | 161 | 127 | 83 | 6 | 2070 | 2.98 | 81.8 | 1.68 | 68.2 | [23 empty] | 0 | 0.12 | 31.94 | 38.6 |  |  |  | 0 | 0.08 | 32.2 | 40 | [10 empty] | 1.09 | 2.2 | 8.1 | 8.7
24 | 130 |  | 150 |  | 82 | 76 | 8 | 1130 | 2710 | 2820 | 2810 | 3330 | 2880 | 3950 | 3940 | 4120 | 3670 | 3770 | 6000 |  | 4800 |  | 179 | 167 | 96 | 105 | 5 | 5180 | 3.06 | 82.9 | 2.02 | 69.9 | [6 empty] | 180 |  | 170 | 120 | 320 | 3100 |  | 3000 | 2200 | 2900 | 7.17 |  | 7.12 | 7.09 | 7 |  |  | 0 | 0.12 | 31.69 | 40.2 |  |  |  | 0 | 0.07 | 31.9 | 38.7 | [10 empty] | 1.43 | 2.65 | 6.8 | 7.5
25 | 136 |  | 190 |  |  |  | 9 | [15 empty] | 148 | 165 |  |  | 4 | [28 empty] | 0 | 0.1 | 30.48 | 39.9 |  |  |  | 0 | 0.06 | 27.9 | 38.7 | [10 empty] | 1.14 | 2.16 | 8.1 | 9
26 | 154 |  | 130 |  |  |  | 9 | [15 empty] | 133 | 137 |  |  | 4 | [28 empty] | 0.03 | 0.08 | 32.18 | 41.9 |  |  |  | 0.03 | 0.06 | 30.6 | 38.1 | [10 empty] | 1.19 | 1.88 | 9.9 | 10.2
27 | 144 |  | 132 |  | 190* | 89 | 9 |  | 2340 | 2370 | 3110 | 3110 | 3070 | 3320 | 2350 | 3110 | 3100 | 3030 | 6900 |  | 10120* |  | 161 | 151 |  |  | 5 | [28 empty] | 0.02 | 0.06 | 31.26 | 39.4 |  |  |  | 0.04 | 0.04 | 30.4 | 38.4 | [10 empty] | 1.02 | 2.64 | 7.6 | 7.8
28 | 160 | 80 | 202 | 81.2 | 62 | 132 | 34 | 1390 | 3480 | 2730 | 3550 | 2770 | 2630 | 4070 | 4740 | 4570 | 3550 | 3160 | 7140 | 81 | 4180 | 82.3 | 68 | 77 | 67 | 68 | 11 | 4620 | 3.08 | 82.1 | 1.9 | 71.4 | [6 empty] | 250 |  | 400 | 140 | 300 | 2800 |  | 2600 | 3000 | 2900 | 7 |  | 6.9 | 7 | 7 |  |  | 0.11 | 0.34 | 17.85 | 27.6 |  |  |  | 0.06 | 0.24 | 17.7 | 26.2 | [10 empty] | 0.96 | 2 | 6.9 | 9.8
29 | 151 |  | 144 |  | 80 | 96 | 7 | 3990 | 3950 | 3020 | 3290 | 3250 | 2810 | 4700 | 5280 | 4310 | 4450 | 4540 | 6980 |  | 5220 |  | 136 | 150 | 76 | 80 | 3 | 5500 | 3.55 | 83 | 1.35 | 72.2 | [21 empty] | 98 | 225 | 0.14 | 0.09 | 28.41 | 40.7 |  |  |  | 0.13 | 0.05 | 27.4 | 36.8 |  |  |  | 0.02 | 0.03 | 22.6 |  |  |  |  | 1.44 | 3.06 | 5.3 | 6.5
30 | 136 | 83.8 | 146 | 79.5 | 64 | 82 | 6 | 2710 | 4310 | 3270 | 3230 | 3350 | 3140 | 4610 | 4600 | 4360 | 3990 | 3980 | 7560 | 78.3 | 5220 | 77 | 139 | 157 | 81 | 80 | 2 | 3610 | 3.6 | 80.6 | 1.55 | 69.2 | [23 empty] | 0.14 | 0.02 | 30.36 | 40.1 |  |  |  | 0.17 | 0 | 29.8 | 38 | [10 empty] | 1.94 | 3.32 | 4.7 | 6.1
31 | 120 |  | 132 |  | 50 | 76 | 6 | 134 | 3720 | 3060 | 4310 | 3700 | 2720 | 4370 | 4390 | 4720 | 4000 | 4480 | 6960 |  | 4700 |  | 151 | 149 | 88 | 93 | 3 | 2210 | 2.97 | 83.1 | 1.89 | 77.6 | [6 empty] | 300 |  | 290 | 360 | 1040 | 3100 |  | 3200 | 2800 | 800 | 7.2 |  | 7.4 | 7.2 | 5.88 |  |  | 0.02 | 0.1 | 31.33 | 38.2 |  |  |  | 0.02 | 0.05 | 30 | 37 | [10 empty] | 1.51 | 3.53 | 5.5 | 6.4
AVG | 148 | 82 | 151 | 81.4 | 76 | 85 | 12 | 680 | 3000 | 2800 | 3200 | 3100 | 2900 | 4200 | 4300 | 4200 | 4400 | 4100 | 6800 | 80 | 5400 | 80.2 | 141 | 148 | 87 | 86 | 6 | 2839 | 3.4 | 82.1 | 1.9 | 69.1 | [6 empty] | 220 |  | 290 | 210 | 340 | 3200 |  | 3300 | 2800 | 3000 | 7.1 |  | 7.1 | 7.1 | 6.9 | 390 | 430 | 0.07 | 0.11 | 28.8 | 38.3 | 2.5 | 4.3 | 374 | 0.07 | 0.08 | 28 | 36.6 | 2.4 | 4.2 | 348 | 0.05 | 0.04 | 22.4 | 27.9 | 2.3 | 4.4 | 223 | 1.19 | 2.55 | 8.7 | 9.9 | 2.3 | 4 | 66 | [30 empty] | #DIV/0! | #DIV/0! |  |  |  |  | AVG
Dewaterubg Sludge well overflow, high concentrated solid sludge recycle back to HL, data were highlined in blue
|  | MISCELLANEOUS |  |  | PRIM. EFF. ALKA. N & S (mg/L) | [9 empty] | GRIT ANALYSIS
|  |  | Date | BOD | Date | Alk (N&S) | pH | [5 empty] | NO.1 |  | NO.2 |  | NO.3 |  | NO.4
|  | INF.HL | 2016-03-02 | 147 | 3/7/16 | 166 | [5 empty] | Date | %Sol | %Vol | %Sol | %Vol | %Sol | %Vol | %Sol | %Vol
|  | Inf.LL |  | 151 | 3/14/16 | 164 | [5 empty] | 3/7/16 | 39.3 | 45.4 | 43.5 | 45.4 | 38.9 | 44.3
|  | EFF. |  | 27 | 3/21/16 | 146 | [5 empty] | 3/14/16 | 42.9 | 41.2 | 41.4 | 42.4 | 41.8 | 43.7
[5 empty] | 3/28/16 | 143 | [5 empty] | 3/21/16 | 48.3 | 37.9 | 45.6 | 40.3 | 45.6 | 41
[12 empty] | 3/28/16 | 43.5 | 43.4 | 46.8 | 37.8 | 43.2 | 43.4
* The blowers are shut down some hours during the 7-3 shifts on 5/5, 5/6, 5/12 and 5/19
* Annual generator load Test taken on 5/13

## LA_
| Bowery Bay Lab Sheet |  |  |  |  | 2016-03-01 |  |  | 2016
| Total Suspended Solids (mg/L) | [21 empty] | Carb. Biochemical Oxygen Demand (mg/L) | [15 empty] | Digester Control | [14 empty] | Chlorides Influent |  | Plant Influent (mg/L) | [13 empty] | Primary Effluent | [6 empty] | Plant Effluent | [6 empty] | Waste Sludge |  |  |  | Waste Sludge |  |  |  | Dewatering Nutrient Analysis | [17 empty] | Dewatering Solids Analysis | [10 empty] | SAMPLE RECEPTION TEMP
D | Raw Sewage |  |  |  | Prim Eff | Prim Eff | Plant | Thick | Aerator Effluent |  |  |  |  | Average Aerator |  |  |  |  | Return Sludge |  | Return Sludge |  | Raw |  | Primary |  | Plant | Thickener | Thickened |  | Primary Dig |  | Secondary Dig |  | Waste Sludge |  |  |  | Digester Volatiles |  |  |  |  | Alkalinity |  |  |  |  | pH |  |  |  |  | (mg/L) |  | High Level | [6 empty] | Lower Level | [6 empty] | (mg/L) | [6 empty] | (mg/L) | [6 empty] | North |  |  |  | South |  |  |  | Treated Centrate (SCT) | [7 empty] | Centrate (mg/L) |  |  |  | Cake (mg/L) | [7 empty] | Cake |  | Centrate |  | Centrate |  |  |  | D |  |  | Nitrogen Analysis
A | High Level |  | Lower Level |  | South | North | Eff | Eff | (mg/L) |  |  |  |  | (mg/L) |  |  |  |  | South |  | North |  | Sewage |  | Effluent |  |  | Feed | Sludge |  | Sludge |  | Sludge |  | South |  | North |  | (mg/L) |  |  |  |  | (mg/L) | [9 empty] | High | Lower | Nitrogen (as N) |  |  |  | Phosphorus |  | Demand | Nitrogen (as N) |  |  |  | Phosphorus |  | Demand | Nitrogen |  |  |  | Phosphorus |  | Demand | Nitrogen |  |  |  | Phosphorus |  | Demand | (mg/L) |  |  |  | (mg/L) |  |  |  | Nitrogen |  |  | Alkalinity | TSS (mg/L) |  |  |  | pH | Nitrogen |  | Phosphorus | PH | Nitrogen |  |  |  | Phosphorus | Sludge Feed |  |  |  | %SOL | %VOL | SS | VOL. SS | CBOD | ALK | A |  |  | NH3 as NH3 (mg/L)
Y | Total | %VOL | Total | %VOL | (mg/L) | (mg/L) | (mg/L) | (mg/L) | NO.1&2 | NO.3&4 | NO.5&6 | NO.7&8 | NO.9&10 | NO.1&2 | NO.3&4 | NO.5&6 | NO.7&8 | NO.9&10 | Total | %VOL | Total | %VOL | H.L. | L.L. | South | North | Effluent | TSS (mg/L) | %SOL | %VOL | %SOL | %VOL | %SOL | %VOL | %SOL | %VOL | %SOL | %VOL | No. 3 | No. 5 | No. 6 | No.7 | No.8 | No. 3 | No. 5 | No. 6 | No.7 | No.8 | No. 3 | No. 5 | No. 6 | No.7 | No.8 | Level | Level | NO2 | NO3 | NH3 | TKN | Ortho | Total | COD | NO2 | NO3 | NH3 | TKN | Ortho | Total | COD | NO2 | NO3 | NH3 | TKN | Ortho | Total | COD | NO2 | NO3 | NH3 | TKN | Ortho | Total | COD | NO2 | NO3 | NH3 | TKN | NO2 | NO3 | NH3 | TKN | NO2 | NO3 | NH3 | [6 empty] | NH3 | Alk | Total |  | NO2 | NO3 | NH3 | TKN | Total | %SOL | %VOL | %SOL | %VOL | Total |  | (mg/L) | % | (mg/L) | (mg/L) | Y |  |  | Infl_HL | Infl_LL | Effluent
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 103 | 104 | 105 | 106 | 107 | 108 | 109 | 110 | 111 | 112 | 113 | 114 | 115 | 116 | 117 | 118 | 119 |  | Celcius | Ice? | 113 | 114 | 115
1 | 119 |  | 120 |  | 50 | 72 | 7 | 160 | 5380 | 6100 | 4970 | 3720 | 2860 | 4310 | 4740 | 5230 | 4740 | 4670 | 7680 |  | 5080 |  | 138 | 162 | 90 | 89 | 5 | 2060 | 3.8 | 79.7 | 2.1 | 69.2 | [21 empty] | 96 | 155 | 0.041 | 0.158 | 22.7 | 37.4 | 2.67 | 4.59 | 373 | 0.035 | 0.123 | 22.8 | 37.4 | 2.57 | 4.46 | 363 | <0.012 | 0.024 | 22.5 | 31.3 | 2.56 | 4.72 | 233 | 0.826 | 2.8 | 9.69 | 12.1 | 1.27 | 1.49 | 47 | [36 empty] | 1 | <6 | yes | 27.56 | 27.69 | 11.77
2 | 136 | 78 | 112 | 80.4 | 84 | 72 | 72 | 176 | 2030 | 2190 | 2050 | 2220 | 2020 | 3550 | 3840 | 3730 | 3500 | 3430 | 7520 | 80.3 | 7860 | 78.4 | 140 | 133 | 68 | 63 | 21 | 2240 | 3.4 | 81.2 | 2.5 | 71 | [23 empty] | 0.116 | 0.243 | 18 | 31.7 |  |  |  | 0.112 | 0.238 | 18.7 | 31 | [10 empty] | 0.858 | 2.73 | 9.32 | 16.2 | [39 empty] | 2 | <6 | yes | 21.86 | 22.71 | 11.32
3 | 124 |  | 151 |  | 54 | 100 | 20 | 96 | 5090 | 2710 | 5110 | 3110 | 3040 | 4630 | 5630 | 5120 | 3970 | 3890 | 5500 |  | 4650 |  | 171 | 191 | 98 | 132 | 8 | 940 | 3.46 | 82 | 2 | 68 | [6 empty] | 190 |  | 140 | 450 | 180 | 3500 |  | 3800 | 3200 | 3000 | 7.1 |  | 7.2 | 6.9 | 7.1 |  |  | 0.128 | 0.137 | 23.8 | 38.7 |  |  |  | 0.113 | 0.101 | 23.3 | 38.3 | [10 empty] | 1.06 | 3.09 | 8.9 | 11.7 | [39 empty] | 3 | <6 | yes | 28.9 | 28.29 | 10.81
4 | 120 |  | 130 |  |  |  | 9 | [15 empty] | 124 | 111 |  |  | 4 | [28 empty] | 0.105 | 0.123 | 22.9 | 35.5 |  |  |  | 0.104 | 0.111 | 22 | 35.8 | [10 empty] | 1.03 | 2.48 | 8.82 | 11.3 | [39 empty] | 4 | <6 | yes | 27.81 | 26.71 | 10.71
5 | 142 |  | 106 |  |  |  | 9 | [15 empty] | 165 | 154 |  |  | 6 | [28 empty] | 0.054 | 0.065 | 25.5 | 39.4 |  |  |  | 0.058 | 0.074 | 25.3 | 38 | [10 empty] | 1.2 | 2.68 | 7.96 | 10.6 | [39 empty] | 5 | <6 | yes | 30.96 | 30.72 | 9.67
6 | 142 |  | 136 |  | 64 | 79 | 10 |  | 2360 | 2250 | 2720 | 3020 | 2600 | 10450 | 3730 | 3330 | 6410 | 6580 | 5840 |  | 4740 |  | 160 | 160 |  |  | 6 | [28 empty] | 0.048 | 0.124 | 25.4 | 39.8 |  |  |  | 0.089 | 0.044 | 25.2 | 37.95 | [10 empty] | 1.11 | 2.08 | 7.87 | 11.1 | [39 empty] | 9 | <6 | yes | 30.84 | 30.6 | 9.56
7 | 146 | 78.1 | 142 | 77.5 | 66 | 76 | 10 | 150 | 2350 | 2550 | 2490 | 2450 | 3150 | 3660 | 4090 | 4290 | 3680 | 3760 | 5860 | 80.9 | 5080 | 79.9 | 107 | 111 | 81 | 82 | 5 | 640 | 3.23 | 83.5 | 1.81 | 67.4 | [6 empty] | 170 |  | 180 | 130 | 130 | 3600 |  | 3800 | 2000 | 3800 | 7.29 |  | 7.36 | 7.12 | 7.2 |  |  | 0.139 | <0.011 | 22.8 | 36.9 |  |  |  | 0.154 | <0.011 | 21.8 | 36.6 | [10 empty] | 1.2 | 1.47 | 9.66 | 12.3 | [39 empty] | 7 | <6 | yes | 27.69 | 26.47 | 11.73
8 | 176 |  | 168 |  | 96 | 78 | 11 | 160 | 3590 | 3270 | 3540 | 2440 | 2030 | 3360 | 3710 | 3580 | 3970 | 3790 | 8060 |  | 5500 |  | 106 | 142 | 106 | 77 | 7 | 960 | 4.16 | 85.6 | 1.92 | 68 | [21 empty] | 137 | 337 | 0.105 | 0.028 | 25.5 | 41.4 |  |  |  | 0.106 | <0.011 | 24 | 37.9 |  |  |  | 0.072 | <0.011 | 25.7 |  |  |  |  | 1.05 | 2.28 | 11 | 13.4 | [39 empty] | 8 | <6 | yes | 30.96 | 29.14 | 13.36
9 | 164 | 82.9 | 168 | 81 | 84 | 70 | 7 | 210 | 2460 | 2470 | 2490 | 3500 | 2900 | 4220 | 4620 | 4380 | 4720 | 4550 | 6500 | 78.2 | 6660 | 77.5 | 148 | 157 | 81 | 82 | 4 | 1760 | 3.5 | 83.3 | 2 | 68.5 | [23 empty] | 0.035 | 0.09 | 23.8 | 39.4 |  |  |  | 0.037 | 0.066 | 23.8 | 39.7 | [10 empty] | 0.968 | 2.76 | 8.23 | 10.5 | [39 empty] | 9 | <6 | yes | 28.9 | 28.9 | 9.99
10 | 152 |  | 158 |  | 66 | 106 | 8 | 120 | 5530 | 2780 | 3350 | 3560 | 3470 | 4890 | 5300 | 5340 | 5780 | 4090 | 6400 |  | 6400 |  | 175 | 181 | 97 | 108 | 6 | 1980 | 3.4 | 81.4 | 1.99 | 68 | [6 empty] | 220 |  | 200 | 190 | 160 | 3100 |  | 3200 | 3100 | 3100 | 7.1 |  | 7.1 | 7.1 | 7.1 |  |  | 0.125 | <0.011 | 22.5 | 37.8 |  |  |  | 0.123 | <0.011 | 22.2 | 37.5 | [10 empty] | 1.2 | 2.7 | 7.11 | 9.86 | [39 empty] | 10 | <6 | yes | 27.32 | 26.96 | 8.63
11 | 152 |  | 140 |  |  |  | 8 | [15 empty] | 145 | 153 |  |  | 7 | [28 empty] | 0.107 | <0.011 | 25.1 | 39.9 |  |  |  | 0.108 | <0.011 | 23.6 | 36.4 | [10 empty] | 1.43 | 2.24 | 7.43 | 10.3 | [39 empty] | 11 | <6 | yes | 30.48 | 28.66 | 9.02
12 | 170 |  | 148 |  |  |  | 8 | [15 empty] | 140 | 137 |  |  | 5 | [28 empty] | 0.115 | 0.029 | 25.2 | 39.1 |  |  |  | 0.12 | <0.011 | 25.3 | 38.1 | [10 empty] | 1.45 | 1.73 | 7.41 | 10.1 | [39 empty] | 12 | <6 | yes | 30.6 | 30.72 | 9
13 | 180 |  | 184 |  | 94 | 74 | 8 |  | 2510 | 2450 | 2830 | 2640 | 2720 | 2440 | 2470 | 2110 | 2550 | 2660 | 6780 |  | 5560 |  | 155 | 154 |  |  | 5 | [28 empty] | 0.046 | 0.081 | 25.7 | 43 |  |  |  | 0.045 | 0.05 | 25.5 | 39.6 | [10 empty] | 1.27 | 3.04 | 6.53 | 9.49 | [39 empty] | 13 | <6 | yes | 31.21 | 30.96 | 7.93
14 | 224 | 78.6 | 220 | 81.8 | 70 | 90 | 24 | 220 | 2440 | 2480 | 2640 | 3150 | 2590 | 4370 | 3720 | 3800 | 3760 | 3950 | 1760 | 80.7 | 4840 | 84.3 | 89 | 95 | 77 | 92 | 11 | 4540 | 2.9 | 85.8 | 1.5 | 68.3 | [6 empty] | 170 |  | 380 | 190 | 320 | 3100 |  | 3500 | 3100 | 3600 | 6.98 |  | 7.1 | 6.99 | 7.06 |  |  | 0.067 | 0.42 | 15 | 29.5 |  |  |  | 0.09 | 0.348 | 14.5 | 27.4 | [10 empty] | 0.859 | 1.84 | 7.19 | 12 | [39 empty] | 14 | <6 | yes | 18.21 | 17.61 | 8.73
15 | 156 |  | 162 |  | 120 | 88 | 15 | 330 | 2660 | 2650 | 2720 | 2550 | 2290 | 4090 | 4310 | 4070 | 4290 | 3920 | 6620 |  | 6660 |  | 108 | 152 | 54 | 66 | 6 | 3220 | 3.5 | 82.4 | 1.8 | 68.2 | [21 empty] | 1520 | 1190 | 0.21 | 0.011 | 17.1 | 33.2 | 2.23 | 4.04 | 375 | 0.195 | 0.058 | 17.1 | 32.82 | 2.2 | 3.84 | 333 | 0.177 | 0.087 | 17.4 | 24.37 | 2.12 | 4.01 | 213 | 1.39 | 2.54 | 5.72 | 9.81 | 3.32 | 6.45 | 84 | [36 empty] | 15 | <6 | yes | 20.76 | 20.76 | 6.95
16 | 144 | 86.1 | 162 | 82.7 | 74 | 68 | 6 | 880 | 3280 | 2930 | 2530 | 2790 | 2780 | 3990 | 3830 | 3270 | 3950 | 4360 | 7700 | 78.2 | 6840 | 78.7 | 129 | 146 | 85 | 68 | 3 | 3680 | 3.91 | 74.5 | 1.8 | 64.4 | [23 empty] | 0.073 | 0.087 | 23.6 | 37.23 |  |  |  | 0.154 | <0.011 | 21.1 | 34.7 | [10 empty] | 1.5 | 3.11 | 6.61 | 8.6 | [39 empty] | 16 | <6 | yes | 28.66 | 25.62 | 8.03
17 | 182 |  | 156 |  | 74 | 102 | 6 | 160 | 3100 | 2980 | 2940 | 3280 | 3100 | 4370 | 5010 | 4080 | 4230 | 4560 | 6700 |  | 5600 |  | 143 | 142 | 82 | 115 | 3 | 2530 | 3.64 | 79.8 | 1.75 | 67.4 | [6 empty] | 210 |  | 440 | 200 | 370 | 3500 |  | 3400 | 2900 | 3500 | 7.2 |  | 7.01 | 7.14 | 7.1 |  |  | 0.019 | 0.123 | 24.6 | 39.2 |  |  |  | 0.018 | 0.092 | 26.2 | 36.2 | [10 empty] | 1.12 | 2.97 | 6.31 | 8.58 | [39 empty] | 17 | <6 | yes | 29.87 | 31.81 | 7.66
18 | 140 |  | 131 |  |  |  | 7 | [15 empty] | 140 | 152 |  |  | 3 | [28 empty] | 0.023 | 0.114 | 23.7 | 39.6 |  |  |  | 0.02 | 0.079 | 23.2 | 37 | [10 empty] | 1.24 | 3.39 | 6.37 | 8.45 | [39 empty] | 18 | <6 | yes | 28.78 | 28.17 | 7.74
19 | 131 |  | 146 |  |  |  | 6 | [15 empty] | 146 | 166 |  |  | 4 | [28 empty] | <0.012 | 0.115 | 26.4 | 41.8 |  |  |  | <0.012 | 0.088 | 25.3 | 39.9 | [10 empty] | 1.1 | 2.89 | 6.78 | 8.83 | [39 empty] | 19 | <6 | yes | 32.06 | 30.72 | 8.23
20 | 128 |  | 132 |  | 82 | 92 | 8 |  | 2590 | 2400 | 3080 | 3250 | 2870 | 4840 | 4000 | 3750 | 7820 | 4420 | 2940 |  | 5480 |  | 183 | 180 |  |  | 4 | [28 empty] | <0.012 | 0.11 | 26.1 | 40.5 |  |  |  | <0.012 | 0.089 | 24.8 | 37.3 | [10 empty] | 1.09 | 2.45 | 7.69 | 10.1 | [39 empty] | 20 | <6 | yes | 31.69 | 30.11 | 9.34
21 | 138 | 84.1 | 156 | 84.6 | 224 | 66 | 10 | 400 | 4510 | 3260 | 5170 | 3770 | 3620 | 4120 | 4990 | 4520 | 5140 | 4200 | 7920 | 82.6 | 3820 | 84.3 | 120 | 131 | 124 | 64 | 6 | 2840 | 2.73 | 82.5 | 1.92 | 68.8 | [6 empty] | 250 |  | 420 | 150 | 220 | 3100 |  | 3000 | 2900 | 3000 | 7 |  | 7 | 7 | 7 |  |  | 0.021 | 0.134 | 23.6 | 38.8 |  |  |  | 0.026 | 0.103 | 21.9 | 34.4 | [10 empty] | 1 | 1.85 | 7.7 | 9.97 | [39 empty] | 21 | <6 | yes | 28.66 | 26.59 | 9.35
22 | 138 |  | 150 |  | 82 | 88 | 9 | 142 | 4440 | 2900 | 4460 | 3470 | 3310 | 5190 | 4660 | 4720 | 4320 | 4330 | 6540 |  | 5000 |  | 161 | 174 | 82 | 96 | 5 | 3360 | 2.78 | 84.3 | 1.9 | 67.3 | [21 empty] | 111 | 224 | <0.012 | 0.134 | 26.6 | 40.9 |  |  |  | 0.014 | 0.103 | 25.4 | 39.3 |  |  |  | <0.012 | 0.05 | 24 |  |  |  |  | 1.34 | 2.52 | 5.73 | 8.42 | [39 empty] | 22 | <6 | yes | 32.3 | 30.84 | 6.96
23 | 164 | 86.6 | 162 | 84 | 102 | 82 | 9 | 360 | 5530 | 3300 | 6600 | 3530 | 2970 | 4960 | 5540 | 5270 | 4640 | 4270 | 8580 | 80 | 5680 | 79.2 | 162 | 161 | 127 | 83 | 6 | 2070 | 2.98 | 81.8 | 1.68 | 68.2 | [23 empty] | <0.012 | 0.115 | 26.3 | 38.6 |  |  |  | <0.012 | 0.08 | 26.5 | 40 | [10 empty] | 1.09 | 2.2 | 6.64 | 8.74 | [39 empty] | 23 | <6 | yes | 31.94 | 32.18 | 8.06
24 | 130 |  | 150 |  | 82 | 76 | 8 | 1130 | 2710 | 2820 | 2810 | 3330 | 2880 | 3950 | 3940 | 4120 | 3670 | 3770 | 6000 |  | 4800 |  | 179 | 167 | 96 | 105 | 5 | 5180 | 3.06 | 82.9 | 2.02 | 69.9 | [6 empty] | 180 |  | 170 | 120 | 320 | 3100 |  | 3000 | 2200 | 2900 | 7.17 |  | 7.12 | 7.09 | 7 |  |  | <0.012 | 0.122 | 26.1 | 40.2 |  |  |  | <0.012 | 0.068 | 26.3 | 38.7 | [10 empty] | 1.43 | 2.65 | 5.58 | 7.48 | [39 empty] | 24 | <6 | yes | 31.69 | 31.94 | 6.78
25 | 136 |  | 190 |  |  |  | 9 | [15 empty] | 148 | 165 |  |  | 4 | [28 empty] | <0.012 | 0.103 | 25.1 | 39.9 |  |  |  | <0.012 | 0.061 | 23 | 38.7 | [10 empty] | 1.14 | 2.16 | 6.65 | 8.99 | [39 empty] | 25 | <6 | yes | 30.48 | 27.93 | 8.08
26 | 154 |  | 130 |  |  |  | 9 | [15 empty] | 133 | 137 |  |  | 4 | [28 empty] | 0.028 | 0.081 | 26.5 | 41.9 |  |  |  | 0.025 | 0.058 | 25.2 | 38.1 | [10 empty] | 1.19 | 1.88 | 8.12 | 10.18 | [39 empty] | 26 | <6 | yes | 32.18 | 30.6 | 9.86
27 | 144 |  | 132 |  | 190 | 89 | 9 |  | 2340 | 2370 | 3110 | 3110 | 3070 | 3320 | 2350 | 3110 | 3100 | 3030 | 6900 |  | 10120 |  | 161 | 151 |  |  | 5 | [28 empty] | 0.023 | 0.061 | 25.74 | 39.4 |  |  |  | 0.035 | 0.036 | 25.03 | 38.4 | [10 empty] | 1.02 | 2.64 | 6.27 | 7.81 | [39 empty] | 27 | <6 | yes | 31.26 | 30.39 | 7.61
28 | 160 | 80 | 202 | 81.2 | 62 | 132 | 34 | 1390 | 3480 | 2730 | 3550 | 2770 | 2630 | 4070 | 4740 | 4570 | 3550 | 3160 | 7140 | 81 | 4180 | 82.3 | 68 | 77 | 67 | 68 | 11 | 4620 | 3.08 | 82.1 | 1.9 | 71.4 | [6 empty] | 250 |  | 400 | 140 | 300 | 2800 |  | 2600 | 3000 | 2900 | 7 |  | 6.9 | 7 | 7 |  |  | 0.112 | 0.343 | 14.7 | 27.6 |  |  |  | 0.059 | 0.239 | 14.6 | 26.2 | [10 empty] | 0.963 | 2 | 5.67 | 9.76 | [39 empty] | 28 | <6 | yes | 17.85 | 17.73 | 6.89
29 | 151 |  | 144 |  | 80 | 96 | 7 | 3990 | 3950 | 3020 | 3290 | 3250 | 2810 | 4700 | 5280 | 4310 | 4450 | 4540 | 6980 |  | 5220 |  | 136 | 150 | 76 | 80 | 3 | 5500 | 3.55 | 83 | 1.35 | 72.2 | [21 empty] | 98 | 225 | 0.14 | 0.092 | 23.4 | 40.7 |  |  |  | 0.129 | 0.053 | 22.6 | 36.8 |  |  |  | 0.018 | 0.031 | 22.6 |  |  |  |  | 1.44 | 3.06 | 4.37 | 6.51 | [39 empty] | 29 | <6 | yes | 28.41 | 27.44 | 5.31
30 | 136 | 83.8 | 146 | 79.5 | 64 | 82 | 6 | 2710 | 4310 | 3270 | 3230 | 3350 | 3140 | 4610 | 4600 | 4360 | 3990 | 3980 | 7560 | 78.3 | 5220 | 77 | 139 | 157 | 81 | 80 | 2 | 3610 | 3.6 | 80.6 | 1.55 | 69.2 | [23 empty] | 0.137 | 0.016 | 25 | 40.1 |  |  |  | 0.169 | <0.011 | 24.5 | 38 | [10 empty] | 1.94 | 3.32 | 3.86 | 6.07 | [39 empty] | 30 | <6 | yes | 30.36 | 29.75 | 4.69
31 | 120 |  | 132 |  | 50 | 76 | 6 | 134 | 3720 | 3060 | 4310 | 3700 | 2720 | 4370 | 4390 | 4720 | 4000 | 4480 | 6960 |  | 4700 |  | 151 | 149 | 88 | 93 | 3 | 2210 | 2.97 | 83.1 | 1.89 | 77.6 | [6 empty] | 300 |  | 290 | 360 | 1040 | 3100 |  | 3200 | 2800 | 800 | 7.2 |  | 7.4 | 7.2 | 5.88 |  |  | 0.018 | 0.1 | 25.8 | 38.2 |  |  |  | 0.021 | 0.049 | 24.7 | 37 | [10 empty] | 1.51 | 3.53 | 4.53 | 6.43 | [39 empty] | 31 | <6 | yes | 31.33 | 29.99 | 5.5
AVG | 148 | 82 | 151 | 81.4 | 88 | 85 | 12 | 680 | 3500 | 2900 | 3500 | 3100 | 2900 | 4500 | 4300 | 4200 | 4400 | 4100 | 6500 | 80 | 5600 | 80.2 | 141 | 148 | 87 | 86 | 6 | 2839 | 3.4 | 82.1 | 1.9 | 69.1 | [6 empty] | 220 |  | 290 | 210 | 340 | 3200 |  | 3300 | 2800 | 3000 | 7.1 |  | 7.1 | 7.1 | 6.9 | 390 | 430 | 0.08 | 0.12 | 23.7 | 38.3 | 2.5 | 4.3 | 374 | 0.08 | 0.1 | 23.1 | 36.6 | 2.4 | 4.2 | 348 | 0.09 | 0.05 | 22.4 | 27.8 | 2.3 | 4.4 | 223 | 1.19 | 2.55 | 7.2 | 9.9 | 2.3 | 4 | 66 | [36 empty] | AVG |  |  | 28.7606 | 28.0229 | 8.6861
SOP# | PCLS1R5-14 | [21 empty] | PCLS3R6-15 |  |  |  |  | PWIS7R2-15 | [10 empty] | NO SOP |  |  |  |  | PCLS11R4-12 | [9 empty] | PWIS13R2-15 |  | PWIS1R3-14 |  |  | PWIS8R2-14 | PCLS7R5-12 |  | PCLS6R8-15 | PWIS1R3-14 |  |  | PWIS8R2-14 | PCLS7R5-12 |  | PCLS6R8-15 | PWIS1R3-14 |  |  | PWIS8R2-14 | PCLS7R5-12 |  | PCLS6R8-15 | PWIS1R3-14 |  |  | PWIS8R2-14 | PCLS7R5-12 |  | PCLS6R7-13 | [8 empty] | PWIS1R3-14 |  |  | PCLS11R4-12 | PCLS1R4-13 | QALW3R0-12 |  |  | QALW3R0-12 | PWIS1R3-14 | PCLS11R4-12 | PCLS7R5-12 | [6 empty] | PWIS7R2-15 | [5 empty] | PCLS1R5-14 |  | PCLS3R6-15 | PWIS8R2-14
|  | MISCELLANEOUS |  |  | PRIM. EFF. ALKA. N & S (mg/L) | [7 empty] | GRIT ANALYSIS TOTAL SOLIDS
|  |  | BOD |  | Date | Alk (N&S) | pH | [5 empty] | NO.1 |  | NO.2 |  | NO.3 |  | NO.4
|  | INF.HL | 2016-03-02 | 147 | 3/7/16 | 166 | [5 empty] | Date | %Sol | %Vol | %Sol | %Vol | %Sol | %Vol | %Sol | %Vol
|  | Inf.LL |  | 151 | 3/14/16 | 164 | [5 empty] | 3/7/16 | 39.3 | 45.4 | 43.5 | 45.4 | 38.9 | 44.3
|  | EFF. |  | 27 | 3/21/16 | 146 | [5 empty] | 3/14/16 | 42.9 | 41.2 | 41.4 | 42.4 | 41.8 | 43.7
[5 empty] | 3/28/16 | 143 | [5 empty] | 3/21/16 | 48.3 | 37.9 | 45.6 | 40.3 | 45.6 | 41
[12 empty] | 3/28/16 | 43.5 | 43.4 | 46.8 | 37.8 | 43.2 | 43.4

## PT_
Bower Bay WPCP PT Sheet
| 2016-03-01 |  |  | 2016-03-01 | 2016 | [44 empty] | Tanks In Service
[50 empty] | Pri | Aer | Aer | Final | Final | Final | Final | Final | Final
D | Effluent | Settleable Solids (ml/L) |  |  | pH | [8 empty] | Fecal Coliform |  |  | Avg Eff | DISSOLVED OXYGEN (mg/L) |  |  |  |  | Cylinder Readings |  | AVG | Thickener | Digester |  | Thickened | Fuel Oil (gal) |  | PURCH GAS | Dig Gas | POWER |  | Process | Centrifuges |  | Sludge | Polymer |  | Centrate |  | Cake Removed |  | Centrate | Digester Sludge |  | Weather | Tanks | Tanks | Tanks | 1,4,8,11 | 2,3,9,10 | 5,7 | 6 | 12,14,15,17 | 13,16 |  |  |  | 1000 | [45 empty] | SCT pH
A | Temperature | Raw Sewage |  | Effluent | Raw Low Level |  |  | Raw High Level |  |  | Final Effluent |  |  | ( >, < | Count | Sample Cl2 | Chlorine | Plant | South |  | North |  | Average | Average | CYL | Polymer | Temp |  | Sludge | To | To | USED | Boilers | (1000 KWH) |  | Air | Units | Oper | Feed | gal from | gal mixed | Totalizer | to boats | Truck | Wet | Flow | From Boat | To Boat | Rain | 0.54 | 2.52 | 2.52 | 0.95 | 0.92 | 1.234 | 1.159 | 1.155 | 1.095 | RAS rate | wasting rate |  | KWH to | NB RAS
Y | °C | Low Level | High Level | Average | Avg | Max | Min | Avg | Max | Min | AVG | MAX | MIN | or E ) | (# FC/100ml) | Residual | Residual | Effluent | AM | PM | AM | PM | South | North | SSV | gal | °F |  | CUFTx1000 | generator | Boiler | CuFt x1000 | CuFt x1000 | PURCH | GEN | MCF/day | in Oper | Hours | gals | Storage | polymer | gal | cuft | Trips | Tons | MGD | cu ft | cu ft | Clear |  | South | North | 0.01 | 0.01 | 0.014 | 0.013 | 0.013 | 0.012 | total | South3 | North | Blowers | to SCT |  | Septage |  |  | gallons * 100 per trip
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 |  | 28 | 29 | 30 | 31 | 32 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 39a | 39b | 40 | 41 | 42 | 43 | 44 | 45 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | [5 empty] | Date | Gallons | trips | day | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 46
1 | 17 |  |  | 0 | 6.9 | 7 | 6.7 | 6.9 | 7 | 6.7 | 6.7 | 7.4 | 6.4 |  | 128 | 0.36 | 0.44 | 4.1 | 3.98 | 4.1 | 4.08 | 4.36 | 280 | 310 | 290 |  | 103 |  | 72 |  |  |  |  | 134.4 |  | 93.8 |  |  |  | 0 | [5 empty] | 0 |  | 79159 | Rain | 14 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 49.5 | 1.7041 | 0.42376 | 53.8042 | 0 | 1 | 36350 | 28 | 1 | 7 | 7 | 30 | 25 | 35 | 8 | 9 | 30 | 25 | 10 | 7 | 2.5 | 3 | 4 | 7 | 30 | 3.5 | 35 | 6 | 6 | 7 | 7 | 5.5 | 3 | 6 | 4 | 35 | 6
2 | 17 |  |  | 0 | 7 | 7.2 | 6.7 | 6.9 | 7.2 | 6.6 | 6.5 | 6.6 | 6.4 |  | 92 | 0.69 | 0.43 | 3.76 | 4.25 | 4.57 | 4.21 | 5.46 | 180 | 280 | 210 |  | 103 |  | 65.7 |  |  |  |  | 131.2 |  | 99.6 |  |  |  | 0 | [5 empty] | 0 |  | 78902 | Rain | 14 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 54.6 | 1.725 | 0.48689 | 57.204 | 0 | 2 | 32150 | 22 | 2 | 1: 6; 2: 7; 3: 35; 4: 30; 5: 35; 6: 22; 7: 35; 8: 7; 9: 30; 10: 6; 11: 6; 12: 3.5; 13: 2.5; 14: 28; 15: 7; 16: 7; 17: 2.5; 18: 7; 19: 27; 20: 7; 21: 4; 22: 7
3 | 17 |  |  | 0 | 6.9 | 7.4 | 6.6 | 6.9 | 7.4 | 6.6 | 6.4 | 6.5 | 6.3 |  | 109 | 0.36 | 0.6 | 4.64 | 4.05 | 3.44 | 5.09 | 4 | 250 | 480 | 330 |  | 104 |  | 63.1 |  |  |  |  | 134.4 |  | 101.4 |  |  |  | 0 | [5 empty] | 0 |  | 39055 | Clear | 14 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 59 | 1.7317 | 0.48306 | 57.4361 | 0 | 3 | 43850 | 28 | 3 | 7 | 30 | 35 | 30 | 35 | 8 | 25 | 28 | 8 | 18 | 3 | 3 | 30 | 3.5 | 35 | 5 | 7 | 20 | 35 | 6 | 4 | 2 | 6 | 7 | 30 | 7 | 6 | 5
4 | 17 |  |  | 0 | 6.9 | 7.2 | 6.6 | 7 | 7.3 | 6.8 | 6.6 | 6.9 | 6.3 |  | 56 | 0.39 | 0.45 | 4.06 | 3.96 | 3.63 | 4.52 | 4.52 | 300 | 790 | 460 |  | 104 |  | 49.9 |  |  |  |  | 134.4 |  | 101.2 |  |  |  | 0 | [5 empty] | 0 |  | 100000 | Snow | 14 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 59.1 | 1.7087 | 0.47551 | 56.316 | 0.16 | 4 | 34810 | 24 | 4 | 6 | 10 | 35 | 9 | 35 | 9 | 3 | 7 | 7 | 30 | 6 | 28 | 6 | 6 | 18.1 | 3 | 25 | 7 | 30 | 11 | 15 | 7 | 5 | 30
5 | 17 |  |  | 0 | 7 | 7.4 | 6.7 | 7 | 7.5 | 6.7 | 6.7 | 6.8 | 6.6 |  | 73 | 0.49 | 0.45 | 4.68 | 4.27 | 3.56 | 6.14 | 5.89 | 320 | 420 | 350 |  | 104 |  | 49.2 |  |  |  |  | 150.4 |  | 99.2 |  |  |  | 0 | [5 empty] | 0 |  |  | Clear | 15 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 59 | 1.69 | 0.46018 | 56.328 | 0.07 | 5 | 28500 | 12 | 5 | 1: 7; 2: 35; 3: 35; 4: 35; 5: 23; 6: 15; 7: 18; 8: 30; 9: 25; 10: 35; 11: 7; 12: 20
6 | 17 |  |  | 0 | 7 | 7.5 | 6.7 | 6.9 | 7.4 | 6.7 | 6.8 | 7.1 | 6.4 |  | 144 | 0.43 | 0.46 | 4.31 | 3.67 | 3.85 | 4.35 | 5.06 | 350 | 460 | 390 |  | 105 |  | 64.7 |  |  |  |  | 140.8 |  | 100.2 |  |  |  | 0 | [5 empty] | 0 |  | 77872 | Clear | 15 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 59 | 1.6506 | 0.42403 | 56.124 | 0.05 | 6 | 7200 | 6 | 6 | 1: 20; 2: 5; 3: 30; 4: 6; 5: 6; 6: 5
7 | 17 |  |  | 0 | 6.9 | 7.1 | 6.7 | 6.9 | 7.2 | 6.6 | 6.6 | 6.8 | 6.5 |  | 88 | 0.33 | 0.46 | 3.75 | 3.49 | 3.6 | 4.25 | 4.37 | 190 | 440 | 270 |  | 105 |  | 48.7 |  |  |  |  | 124.8 |  | 101.1 |  |  |  | 0 | [5 empty] | 0 |  |  | Clear | 15 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 59 | 1.652 | 0.45842 | 56.3801 | 0.02 | 7 | 58800 | 29 | 7 | 6 | 4 | 35 | 30 | 30 | 35 | 30 | 25 | 30 | 6 | 35 | 25 | 35 | 3 | 35 | 30 | 3.5 | 30 | 10 | 30 | 6 | 2.5 | 5 | 30 | 30 | 5 | 3 | 4 | 35
8 | 17 |  |  | 0 | 6.9 | 7.3 | 6.6 | 6.9 | 7.4 | 6.6 | 6.7 | 6.8 | 6.6 |  | 96 | 0.22 | 0.6 | 3.69 | 3.21 | 3.89 | 3.34 | 3.93 | 220 | 320 | 250 |  | 106 |  | 70.1 |  |  |  |  | 131.2 |  | 98.1 |  |  |  | 0 | [5 empty] | 0 |  | 102672 | Clear | 15 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 58.7 | 1.6486 | 0.47051 | 56.4158 | 0 | 8 | 38450 | 28 | 8 | 6 | 7 | 6 | 9 | 35 | 30 | 10 | 5 | 2.5 | 10 | 25 | 3 | 60 | 3.5 | 7 | 3 | 7 | 7 | 5 | 5 | 5 | 30 | 30 | 30 | 28 | 4 | 6 | 5.5
9 | 18 |  |  | 0 | 6.9 | 7.2 | 6.5 | 6.9 | 7.5 | 6.6 | 6.5 | 6.6 | 6.4 |  | 53 | 0.54 | 0.42 | 4.42 | 3.99 | 4.02 | 4.48 | 4.78 | 170 | 480 | 270 |  | 107 |  | 72.4 |  |  |  |  | 131.2 |  | 98.1 |  |  |  | 0 | [5 empty] | 0 |  |  | Clear | 14 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 58.9 | 1.6856 | 0.46812 | 54.372 | 0 | 9 | 44150 | 26 | 9 | 6 | 7 | 7 | 35 | 9 | 2 | 30 | 22 | 35 | 35 | 30 | 3 | 5 | 9 | 6 | 33 | 30 | 7 | 10 | 35 | 1.5 | 30 | 35 | 5 | 7 | 7 | [14 empty] | 9.06
10 | 18 |  |  | 0 | 6.8 | 7.1 | 6.6 | 6.8 | 7.2 | 6.6 | 6.6 | 6.7 | 6.5 |  | 98 | 0.38 | 0.41 | 3.56 | 3.73 | 4.2 | 3.75 | 4.37 | 290 | 420 | 330 |  | 108 |  | 66.8 |  |  |  |  | 131.2 |  | 95.6 |  |  |  | 0 | [5 empty] | 0 |  | 90000 | Clear | 14 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 58.8 | 1.6873 | 0.51148 | 55.6121 | 0 | 10 | 72750 | 40 | 10 | 6 | 3 | 35 | 8 | 30 | 35 | 35 | 8 | 5 | 7 | 18 | 3 | 35 | 7 | 25 | 7 | 3 | 30 | 30 | 6 | 30 | 7 | 8 | 35 | 35 | 35 | 4 | 35 | 35 | 20 | 30 | 30 | 3 | 25 | 5.5 | 6 | 30 | 7 | 5 | 6 | 9.17
11 | 18 |  |  | 0 | 7 | 7.7 | 6.7 | 7 | 7.5 | 6.7 | 6.6 | 6.7 | 6.4 |  | 160 | 0.38 | 0.45 | 4.02 | 3.31 | 4.06 | 4.06 | 4.43 | 210 | 370 | 260 |  | 108 |  | 56.8 |  |  |  |  | 124.8 |  | 100.8 |  |  |  | 0 | [5 empty] | 0 |  | 75500 | Rain | 14 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 59 | 1.7036 | 0.57814 | 57.5119 | 0.11 | 11 | 39800 | 21 | 11 | 1: 35; 2: 30; 3: 10; 4: 30; 5: 6; 6: 30; 7: 35; 8: 9; 9: 10; 10: 5; 11: 35; 12: 8; 13: 2; 14: 15; 15: 30; 16: 35; 17: 35; 18: 6; 19: 15; 20: 10; 21: 7 | 5.17
12 | 18 |  |  | 0 | 6.9 | 7.1 | 6.7 | 6.9 | 7.1 | 6.7 | 6.7 | 6.9 | 6.5 |  | 48 | 0.48 | 0.45 | 4.96 | 3.96 | 3.85 | 3.67 | 4.19 | 220 | 390 | 280 |  | 104 |  | 46 |  |  |  |  | 128 |  | 97.7 |  |  |  | 0 | [5 empty] | 0 |  |  | Clear | 14 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 59 | 1.6989 | 0.51506 | 56.2159 | 0 | 12 | 22800 | 11 | 12 | 1: 7; 2: 25; 3: 15; 4: 21; 5: 25; 6: 30; 7: 35; 8: 30; 9: 3; 10: 30; 11: 7 | 5.23
13 | 18 |  |  | 0 | 6.9 | 7.2 | 6.3 | 6.8 | 7.1 | 6.7 | 6.7 | 6.9 | 6.6 |  | 104 | 0.41 | 0.44 | 3.96 | 4.04 | 4.03 | 3.86 | 4.17 | 210 | 350 | 260 |  | 107 | # | 43.9 |  |  |  |  | 147.2 |  | 98.8 |  |  |  | 0 | [5 empty] | 0 |  | 38500 | Clear | 14 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 59 | 1.6961 | 0.49299 | 56.3719 | 0 | 13 | 9650 | 8 | 13 | 1: 5; 2: 3.5; 3: 35; 4: 5; 5: 3; 6: 35; 7: 5; 8: 5 | 5.28
14 | 16 |  |  | 0 | 7.1 | 7.6 | 6.8 | 7.1 | 7.4 | 6.9 | 6.6 | 6.8 | 6.5 | > | 4000 | 0.21 | 0.51 | 3.52 | 4.08 | 3.89 | 3.56 | 3.96 | 170 | 320 | 220 |  | 104 |  | 86.3 |  |  |  |  | 105.6 |  | 101.2 |  |  |  | 0 | [5 empty] | 0 |  | 40000 | Rain | 14 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 59.5 | 1.7148 | 0.56289 | 56.6921 | 0 | 14 | 43350 | 24 | 14 | 3.5 | 30 | 35 | 10 | 30 | 30 | 3 | 7 | 35 | 20 | 35 | 4 | 7 | 30 | 30 | 10 | 7 | 2 | 30 | 30 | 30 | 5 | 5 | 5 | [16 empty] | 8.94
15 | 18 |  |  | 0 | 6.9 | 7.1 | 6.9 | 7 | 7.2 | 6.7 | 6.7 | 6.8 | 6.4 |  | 156 | 0.23 | 0.45 | 4.26 | 4.79 | 4.6 | 4.85 | 5.6 | 140 | 250 | 180 |  | 102 |  | 59.2 |  |  |  |  | 166.4 |  | 95.4 |  |  |  | 0 | [5 empty] | 0 |  | 199242 | Clear | 14 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 57.8 | 1.7049 | 0.56018 | 55.0399 | 0 | 15 | 37450 | 29 | 15 | 7 | 6 | 7 | 35 | 2 | 35 | 35 | 10 | 6.5 | 35 | 9 | 3 | 7 | 4 | 2 | 20 | 2 | 7 | 7 | 30 | 7 | 7 | 7 | 30 | 5 | 5 | 4 | 35 | 5 | [11 empty] | 8.63
16 | 19 |  |  | 0 | 6.9 | 7.2 | 6.7 | 7 | 7.3 | 6.8 | 6.6 | 6.9 | 6.4 |  | 30 | 0.43 | 0.46 | 4.42 | 4.33 | 4.15 | 3.96 | 3.55 | 190 | 290 | 220 |  | 100 |  | 81.9 |  |  |  |  | 124.8 |  | 96.3 |  |  |  | 0 | [5 empty] | 0 |  | 57000 | Rain | 14 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 57.8 | 1.6392 | 0.50774 | 54.3641 | 0 | 16 | 33950 | 22 | 16 | 1: 7; 2: 35; 3: 30; 4: 35; 5: 10; 6: 6; 7: 5; 8: 5; 9: 25; 10: 15; 11: 7; 12: 25; 13: 10; 14: 30; 15: 7; 16: 2.5; 17: 30; 18: 7; 19: 30; 20: 7; 21: 4; 22: 7 | 8.6
17 | 19 |  |  | 0 | 6.9 | 7.2 | 6.7 | 6.9 | 7.3 | 6.7 | 6.5 | 6.7 | 6.2 |  | 34 | 0.32 | 0.46 | 4.43 | 3.95 | 4.06 | 4.09 | 2.64 | 230 | 350 | 270 |  | 102 | # | 62.4 |  |  |  |  | 131.2 |  | 93.5 |  |  |  | 0 | [5 empty] | 0 |  | 91678 | Clear | 14 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 61.8 | 1.7069 | 0.58505 | 52.2079 | 0 | 17 | 9700 | 13 | 17 | 1: 3; 2: 7; 3: 5; 4: 20; 5: 2; 6: 20; 7: 7; 8: 5; 9: 4; 10: 5; 11: 6; 12: 6; 13: 7 | 8.74
18 | 18 |  |  | 0 | 6.9 | 7.2 | 6.7 | 6.9 | 7.3 | 6.7 | 6.4 | 6.6 | 6.1 |  | 38 | 0.28 | 0.47 | 4.23 | 4.04 | 4.06 | 3.17 | 3.54 | 200 | 350 | 250 |  | 96 | # | 42.5 |  |  |  |  | 128 |  | 95.9 |  |  |  | 0 | [5 empty] | 0 |  | 69835 | Clear | 13 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 61.6 | 1.6983 | 0.66291 | 54.5122 | 0 | 18 | 33150 | 19 | 18 | 1: 5; 2: 6; 3: 30; 4: 35; 5: 12; 6: 8; 7: 8; 8: 35; 9: 30; 10: 6; 11: 7; 12: 10; 13: 30; 14: 20; 15: 25; 16: 2.5; 17: 7; 18: 30; 19: 25 | 9.44
19 | 18 |  |  | 0 | 6.7 | 6.9 | 6.5 | 6.7 | 6.8 | 6.6 | 6.5 | 6.8 | 6.3 |  | 7 | 0.45 | 0.45 | 4.42 | 3.91 | 3.51 | 3.6 | 3.55 | 210 | 380 | 270 |  | 96 | # | 51.6 |  |  |  |  | 131.2 |  | 100.4 |  |  |  | 0 | [5 empty] | 0 |  |  | Clear | 13 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 61.6 | 1.6902 | 0.66291 | 55.1839 | 0 | 19 | 22000 | 9 | 19 | 1: 15; 2: 35; 3: 30; 4: 30; 5: 10; 6: 35; 7: 20; 8: 35; 9: 10 | 5.23
20 | 18 |  |  | 0 | 6.9 | 7.5 | 6.7 | 6.8 | 7.4 | 6.6 | 6.5 | 6.6 | 6.4 |  | 4 | 0.47 | 0.4 | 4.24 | 2.78 | 3.85 | 2.55 | 3.61 | 200 | 380 | 260 |  | 97 | # | 49.9 |  |  |  |  | 134.4 |  | 98.8 |  |  |  | 0 | [5 empty] | 0 |  |  | Snow | 13 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 62.9 | 1.8221 | 0.66291 | 55.7239 | 0 | 20 | 6300 | 6 | 20 | 1: 7; 2: 32; 3: 5; 4: 7; 5: 5; 6: 7 | 8.79
21 | 18 |  |  | 0 | 6.9 | 7.2 | 6.7 | 6.8 | 7.1 | 6.6 | 6.6 | 6.7 | 6.4 |  | 38 | 0.34 | 0.46 | 3.62 | 3.76 | 3.58 | 3.58 | 3.74 | 310 | 400 | 340 |  | 98 |  | 104.2 |  |  |  |  | 137.6 |  | 98.8 |  |  |  | 0 | [5 empty] | 0 |  | 172595 | Snow/Clear | 13 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 62.9 | 1.8221 | 0.66291 | 54.7639 | 0 | 21 | 34500 | 24 | 21 | 30 | 6 | 10 | 7 | 30 | 3 | 30 | 30 | 10 | 35 | 10 | 30 | 3 | 7 | 12 | 10 | 4 | 19 | 35 | 4 | 10 | 5 | 4 | 1 | [16 empty] | 5.37
22 | 18 |  |  | 0 | 6.8 | 7.3 | 6.4 | 6.8 | 7.2 | 6.5 | 6.6 | 6.7 | 6.4 |  | 13 | 0.44 | 0.45 | 4.03 | 3.88 | 3.84 | 3.19 | 3.76 | 300 | 450 | 350 |  | 99 | # | 91.7 |  |  |  |  | 128 |  | 98.8 |  |  |  | 0 | [5 empty] | 0 |  | 56423 | Clear | 13 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 61.1 | 1.7278 | 0.66291 | 54.6202 | 0 | 22 | 29250 | 23 | 22 | 1: 6; 2: 6.5; 3: 6; 4: 30; 5: 30; 6: 35; 7: 8; 8: 4; 9: 6; 10: 5; 11: 35; 12: 30; 13: 5; 14: 7; 15: 7; 16: 7; 17: 7; 18: 7; 19: 30; 20: 5; 21: 6; 22: 4; 23: 6 | 8.78
23 | 19 |  |  | 0 | 6.7 | 7 | 6.3 | 6.7 | 7.2 | 6.4 | 6.5 | 6.6 | 6.4 |  | 37 | 0.41 | 0.5 | 3.93 | 2.91 | 3.69 | 2.16 | 2.5 | 330 | 270 | 310 |  | 101 | # | 59.4 |  |  |  |  | 137.6 |  | 96.5 |  |  |  | 0 | [5 empty] | 0 |  |  | Clear | 13 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 61 | 1.6857 | 0.6278 | 54.912 | 0 | 23 | 38700 | 23 | 23 | 1: 6; 2: 35; 3: 30; 4: 5; 5: 3; 6: 9; 7: 30; 8: 35; 9: 15; 10: 10; 11: 5; 12: 7; 13: 4; 14: 6; 15: 30; 16: 5; 17: 10; 18: 30; 19: 35; 20: 7; 21: 5; 22: 35; 23: 30 | 8.9
24 | 18 |  |  | 0 | 6.9 | 7.5 | 6.6 | 6.9 | 7.6 | 6.5 | 6.5 | 6.6 | 6.2 |  | 117 | 0.23 | 0.44 | 3.94 | 3.92 | 3.55 | 3.54 | 4.72 | 270 | 460 | 330 |  | 100 | # | 44.7 |  |  |  |  | 128 |  | 93.5 |  |  |  | 0 | [5 empty] | 0 |  | 50599 | Clear | 13 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 60.9 | 1.7056 | 0.66872 | 56.88 | 0.13 | 24 | 60500 | 32 | 24 | 3 | 35 | 35 | 2.5 | 35 | 30 | 5 | 7 | 3.5 | 30 | 2 | 6 | 15 | 6 | 6 | 7 | 7 | 7 | 35 | 35 | 30 | 35 | 35 | 7 | 35 | 28 | 35 | 35 | 35 | 5 | 6 | 7 | [8 empty] | 8.57
25 | 18 |  |  | 0 | 6.7 | 7 | 6.4 | 6.7 | 7.1 | 6.5 | 6.5 | 6.6 | 6.3 |  | 40 | 0.23 | 0.44 | 4.05 | 3.59 | 3.97 | 3.38 | 3.42 | 480 | 420 | 460 |  | 104 |  | 51.6 |  |  |  |  | 115.2 |  | 90.7 |  |  |  | 0 | [5 empty] | 0 |  | 175500 | Rain | 13 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 60.8 | 1.7077 | 0.70363 | 55.0402 | 0 | 25 | 35950 | 25 | 25 | 6 | 10 | 6 | 10 | 30 | 30 | 15 | 7 | 2.5 | 10 | 15 | 30 | 4 | 3 | 5 | 25 | 3 | 6 | 30 | 30 | 7 | 25 | 5 | 35 | 10 | [15 empty] | 8.75
26 | 19 |  |  | 0 | 6.7 | 6.8 | 6.6 | 6.8 | 7 | 6.6 | 6.5 | 6.6 | 6.4 |  | 58 | 0.53 | 0.46 | 4.28 | 3.79 | 3.39 | 3.28 | 2.93 | 510 | 590 | 540 |  | 104 | # | 64.5 |  |  |  |  | 128 |  | 92.5 |  |  |  | 0 | [5 empty] | 0 |  | 77196 | Clear | 13 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 60.4 | 1.6922 | 0.7099 | 55.884 | 0 | 26 | 24600 | 10 | 26 | 1: 20; 2: 7; 3: 35; 4: 35; 5: 35; 6: 25; 7: 30; 8: 35; 9: 20; 10: 4 | 8.75
27 | 18 |  |  | 0 | 6.9 | 7.2 | 6.7 | 7 | 7.3 | 6.6 | 6.9 | 7.1 | 6.6 |  | 63 | 0.45 | 0.44 | 3.79 | 3.69 | 3.89 | 3.93 | 3.27 | 460 | 630 | 520 |  | 103 |  | 87 |  |  |  |  | 147.2 |  | 94.6 |  |  |  | 0 | [5 empty] | 0 |  |  | Clear | 13 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 60.1 | 1.7016 | 0.6918 | 55.5761 | 0 | 27 | 13000 | 9 | 27 | 1: 7; 2: 4; 3: 27; 4: 35; 5: 5; 6: 35; 7: 7; 8: 5; 9: 5 | 6.46
28 | 17 |  |  | 0 | 6.8 | 7.1 | 6.6 | 6.9 | 7.2 | 6.6 | 6.5 | 7 | 6.1 | > | 4000 | 0.22 | 0.47 | 2.47 | 3.29 | 4.4 | 2.42 | 5.08 | 450 | 340 | 410 |  | 100 | # | 41.4 |  |  |  |  | 131.2 |  | 92.9 |  |  |  | 0 | [5 empty] | 0 |  | 84499 | Rain | 13 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 60 | 1.7106 | 0.67887 | 54.7039 | 0.17 | 28 | 46900 | 27 | 28 | 7 | 6 | 25 | 35 | 30 | 30 | 6 | 30 | 25 | 8 | 3 | 5 | 25 | 20 | 3.5 | 30 | 6 | 25 | 35 | 35 | 30 | 10 | 2.5 | 15 | 12 | 5 | 5
29 | 18 |  |  | 0 | 6.9 | 7.1 | 6.7 | 7 | 7.2 | 6.7 | 6.6 | 6.9 | 6.4 |  | 120 | 0.29 | 0.43 | 4.41 | 4.19 | 3.98 | 3.67 | 3.72 | 530 | 430 | 500 |  | 102 | # | 71.5 |  |  |  |  | 140.8 |  | 88.4 |  |  |  | 0 | [5 empty] | 0 |  | 109000 | Clear | 13 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 58.8 | 1.7062 | 0.69087 | 55.6481 | 0.12 | 29 | 32250 | 26 | 29 | 7 | 30 | 30 | 5 | 30 | 15 | 5 | 4 | 6 | 3 | 6 | 6 | 35 | 10 | 7 | 5 | 4 | 5 | 4 | 3 | 3 | 30 | 30 | 8 | 25.5 | 6
30 | 17 |  |  | 0 | 6.9 | 7.1 | 6.7 | 6.8 | 7.3 | 6.6 | 6.5 | 6.8 | 6.2 |  | 9 | 0.28 | 0.43 | 4.38 | 3.94 | 3.93 | 2.28 | 4.31 | 480 | 400 | 450 |  | 103 |  | 128 |  |  |  |  | 137.6 |  | 93.5 |  |  |  | 0 | [5 empty] | 0 |  | 104000 | Clear | 13 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 58.5 | 1.7882 | 0.70573 | 56.0801 | 0.17 | 30 | 26700 | 20 | 30 | 1: 4; 2: 2; 3: 35; 4: 6; 5: 30; 6: 35; 7: 30; 8: 5; 9: 2; 10: 5; 11: 10; 12: 3; 13: 35; 14: 5; 15: 30; 16: 4; 17: 8; 18: 3; 19: 10; 20: 5
31 | 19 |  |  | 0 | 6.8 | 7 | 6.5 | 6.8 | 7.3 | 6.6 | 6.4 | 6.6 | 6.1 |  | 18 | 0.46 | 0.42 | 4.46 | 3.95 | 3.9 | 3.61 | 2.57 | 410 | 340 | 390 |  | 103 |  | 90.4 |  |  |  |  | 124.8 |  | 88.8 |  |  |  | 0 | [5 empty] | 0 |  | 86000 | Clear | 13 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 58.4 | 1.892 | 0.68616 | 54.9161 | 0.13 | 31 | 51500 | 30 | 31 | 7 | 10 | 7 | 30 | 25 | 35 | 30 | 35 | 30 | 6 | 30 | 20 | 5 | 7 | 5 | 30 | 30 | 35 | 3 | 5 | 20 | 10 | 5 | 4 | 30 | 35 | 6 | 8 | 5 | 7
[43 empty] | cuft centrate to boat | [6 empty] | 14 | 6 | 3 | 3 | 4 | 1 | 1 | 4 | 1 | 59.3065 | 1.7129 | 0.57877 | 55.5755 | 0.036452 | Total | 1049010 | 654
[7 empty] | effluent flows | [35 empty] | info from marine section |  |  |  |  | info from marine section | [15 empty] | max | 72750 | 40
| readings from DCS system | [5 empty] | process air cfm | [21 empty] | Bold: sludge production were calculated from thickener blanket readings. | [30 empty] | ~0.6mgd of south battery secondary activated sludge was wasted thru TWAS pump #3 to thickener started on 09/10/2012 - 1/7/2013
| (unless noted otherwise) | [5 empty] | blowers kwh | [31 empty] | Bold: Sludge feed and polymer solution used were calculated from feed pumps.
swas rate south and north
[7 empty] | Return Active Sludge (RAS) rate --- started Feb 2014 | [54 empty] | MG per month | avg mgd
[61 empty] | raw cent | 0.0013906 | 4.4858e-05
| (started march 2013, report manager was used rather than trending and save as text from DCS system) | [59 empty] | cent N | 0.2982 | 0.0096193
[61 empty] | cent S | 0.83315 | 0.026876
[61 empty] | RAS to 10 | 1.13 | 0.03645

## DF_
BOWERY BAY -- HOURLY FLOW | [15 empty] | 2016-03-01 |  |  | 2016 | [13 empty] | Bowery Bay High Level Hourly Flow Data | [15 empty] | 2016-03-01 |  |  | 2016 | [9 empty] | Bowery Bay Lower Level Hourly Flow Data | [15 empty] | 2016-03-01 |  |  | 2016 | [35 empty] | Bowery Bay WPCP -- Daily Average Flow Summary
SPDES PERMIT# NY0026158
[114 empty] | TOTAL BYPASS |  |  | D | Daily | Dry | Max | Min | Aerator | Secondary | High | Lower | High | Lower
| AM |  |  |  | AM | Noon | PM | [9 empty] | PM | Midnt | AM | [9 empty] | 7-6 PM | 7-6 AM | Total |  | AM |  |  |  | AM | Noon | PM | [9 empty] | PM | Midnt | AM | [5 empty] | DAILY | DAILY | DAILY |  |  | AM |  |  |  | AM | Noon | PM | [9 empty] | PM | Midnt | AM | [5 empty] | DAILY | DAILY | DAILY |  | AM |  |  |  | AM | Noon | PM | [9 empty] | PM | Midnt | AM | [5 empty] | TOTAL |  |  | A | Raw | Weather | Flow | Flow | Flow | Bypass | Level | Level | Level | Level
DATE | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | AVG | MAX | MIN | DRY | Aer | Aer | Aer | DATE | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | AVG | MAX | MIN |  | DATE | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | AVG | MAX | MIN | DATE | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | MG | max | min | Y | Flow | Flow |  |  |  | Flow | Flow | Flow | % Flow | % Flow
1 | 60 | 78 | 95 | 96 | 96 | 95 | 94 | 87 | 87 | 85 | 87 | 75 | 65 | 68 | 98 | 111 | 112 | 109 | 104 | 91 | 88 | 96 | 121 | 156 | 94 | 156 | 60 | 86 | 86.25 | 101.5833 | 94 | 1 | [28 empty] | 1 | [27 empty] | 1 | [25 empty] | 0 | 0 | 1 | 94 | 86 | 156 | 60 | 94 |  | 61.1 | 32.9 | 0.65 | 0.35
2 | 171 | 165 | 154 | 124 | 111 | 101 | 102 | 74 | 75 | 76 | 78 | 74 | 86 | 111 | 107 | 107 | 108 | 105 | 102 | 98 | 73 | 60 | 47 | 48 | 98 | 171 | 47 | 85 | 108.75 | 87.6667 | 98 | 2 | [28 empty] | 2 | [27 empty] | 2 | [25 empty] | 0 | 0 | 2 | 98 | 85 | 171 | 47 | 98 |  | 63.7 | 34.3 | 0.65 | 0.35
3 | 48 | 57 | 77 | 83 | 92 | 93 | 94 | 94 | 94 | 93 | 95 | 94 | 95 | 94 | 96 | 96 | 97 | 96 | 86 | 74 | 66 | 60 | 52 | 52 | 82 | 97 | 48 | 82 | 84.5 | 80.3333 | 82 | 3 | [28 empty] | 3 | [27 empty] | 3 | [25 empty] | 0 | 0 | 3 | 82 | 82 | 97 | 48 | 82 |  | 53.3 | 28.7 | 0.65 | 0.35
4 | 56 | 86 | 105 | 104 | 102 | 97 | 101 | 111 | 137 | 146 | 139 | 115 | 99 | 100 | 101 | 101 | 95 | 84 | 83 | 80 | 77 | 75 | 55 | 43 | 96 | 146 | 43 | 90 | 108.25 | 82.75 | 96 | 4 | [28 empty] | 4 | [27 empty] | 4 | [25 empty] | 0 | 0 | 4 | 96 | 90 | 146 | 43 | 96 |  | 62.4 | 33.6 | 0.65 | 0.35
5 | 42 | 44 | 51 | 63 | 84 | 100 | 108 | 108 | 108 | 108 | 108 | 107 | 102 | 102 | 102 | 103 | 101 | 88 | 85 | 84 | 81 | 78 | 72 | 45 | 86 | 108 | 42 | 86 | 85.9167 | 86.9167 | 86 | 5 | [28 empty] | 5 | [27 empty] | 5 | [25 empty] | 0 | 0 | 5 | 86 | 86 | 108 | 42 | 86 |  | 55.9 | 30.1 | 0.65 | 0.35
6 | 44 | 55 | 60 | 86 | 94 | 95 | 97 | 99 | 99 | 101 | 103 | 105 | 108 | 98 | 90 | 93 | 96 | 96 | 93 | 87 | 76 | 69 | 61 | 59 | 86 | 108 | 44 | 86 | 86.5 | 85.5 | 86 | 6 | [28 empty] | 6 | [27 empty] | 6 | [25 empty] | 0 | 0 | 6 | 86 | 86 | 108 | 44 | 86 |  | 55.9 | 30.1 | 0.65 | 0.35
7 | 59 | 88 | 95 | 97 | 104 | 106 | 104 | 98 | 97 | 101 | 87 | 89 | 91 | 99 | 104 | 110 | 105 | 101 | 67 | 59 | 45 | 41 | 38 | 32 | 84 | 110 | 32 | 84 | 93.75 | 74.3333 | 84 | 7 | [28 empty] | 7 | [27 empty] | 7 | [25 empty] | 0 | 0 | 7 | 84 | 84 | 110 | 32 | 84 |  | 54.6 | 29.4 | 0.65 | 0.35
8 | 77 | 99 | 100 | 98 | 98 | 97 | 96 | 95 | 92 | 86 | 88 | 89 | 90 | 92 | 93 | 96 | 94 | 94 | 83 | 78 | 77 | 73 | 54 | 53 | 87 | 100 | 53 | 87 | 92.9167 | 81.4167 | 87 | 8 | [28 empty] | 8 | [27 empty] | 8 | [25 empty] | 0 | 0 | 8 | 87 | 87 | 100 | 53 | 87 |  | 56.55 | 30.45 | 0.65 | 0.35
9 | 54 | 59 | 78 | 93 | 92 | 95 | 109 | 105 | 109 | 112 | 86 | 88 | 104 | 108 | 110 | 107 | 105 | 107 | 85 | 85 | 81 | 78 | 72 | 81 | 92 | 112 | 54 | 92 | 90 | 93.5833 | 92 | 9 | [28 empty] | 9 | [27 empty] | 9 | [25 empty] | 0 | 0 | 9 | 92 | 92 | 112 | 54 | 92 |  | 59.8 | 32.2 | 0.65 | 0.35
10 | 80 | 74 | 85 | 64 | 81 | 84 | 89 | 96 | 111 | 106 | 100 | 103 | 95 | 94 | 93 | 99 | 100 | 100 | 100 | 89 | 78 | 75 | 81 | 81 | 90 | 111 | 64 | 90 | 89.4167 | 90.4167 | 90 | 10 | [28 empty] | 10 | [27 empty] | 10 | [25 empty] | 0 | 0 | 10 | 90 | 90 | 111 | 64 | 90 |  | 58.5 | 31.5 | 0.65 | 0.35
11 | 81 | 85 | 93 | 97 | 102 | 101 | 102 | 100 | 99 | 98 | 98 | 98 | 98 | 98 | 98 | 99 | 89 | 89 | 81 | 73 | 71 | 64 | 54 | 47 | 88 | 102 | 47 | 88 | 96.1667 | 80.0833 | 88 | 11 | [28 empty] | 11 | [27 empty] | 11 | [25 empty] | 0 | 0 | 11 | 88 | 88 | 102 | 47 | 88 |  | 57.2 | 30.8 | 0.65 | 0.35
12 | 44 | 44 | 50 | 74 | 95 | 98 | 101 | 103 | 103 | 104 | 104 | 104 | 104 | 103 | 102 | 101 | 100 | 96 | 87 |  | 84 | 76 | 62 | 59 | 87 | 104 | 44 | 87 | 85.3333 | 88.5455 | 87 | 12 | [28 empty] | 12 | [27 empty] | 12 | [25 empty] | 0 | 0 | 12 | 87 | 87 | 104 | 44 | 87 |  | 56.55 | 30.45 | 0.65 | 0.35
13 | 51 | 50 | 58 | 74 | 77 | 82 | 93 | 103 | 103 | 104 | 106 | 104 | 103 | 103 | 103 | 105 | 103 | 102 | 101 | 90 | 79 | 74 | 65 | 44 | 87 | 106 | 44 | 87 | 83.75 | 89.3333 | 87 | 13 | [28 empty] | 13 | [27 empty] | 13 | [25 empty] | 0 | 0 | 13 | 87 | 87 | 106 | 44 | 87 |  | 56.55 | 30.45 | 0.65 | 0.35
14 | 46 | 59 | 123 | 236 | 221 | 202 | 180 | 156 | 161 | 168 | 167 | 156 | 151 | 148 | 135 | 134 | 131 | 129 | 121 | 112 | 97 | 83 | 67 | 69 | 136 | 236 | 46 | 89 | 155.3333 | 114.75 | 135 | 14 | [28 empty] | 14 | [27 empty] | 14 |  |  |  | 11 | [20 empty] | 11 | 11 | 11 | 14 | 136 | 89 | 236 | 46 | 135 | 11 | 88.4 | 47.6 | 0.65 | 0.35
15 | 87 | 115 | 123 | 123 | 121 | 116 | 110 | 95 | 94 | 108 | 122 | 118 | 120 | 115 | 102 | 107 | 104 | 93 | 59 | 51 | 44 | 33 | 57 | 82 | 96 | 123 | 33 | 96 | 111 | 80.5833 | 96 | 15 | [28 empty] | 15 | [27 empty] | 15 | [25 empty] | 0 | 0 | 15 | 96 | 96 | 123 | 33 | 96 |  | 62.4 | 33.6 | 0.65 | 0.35
16 | 78 | 62 | 62 | 87 | 103 | 101 | 101 | 99 | 98 | 95 | 91 | 82 | 85 | 90 | 96 | 101 | 102 | 102 | 99 | 92 | 70 | 58 | 55 | 54 | 86 | 103 | 54 | 86 | 88.25 | 83.6667 | 86 | 16 | [28 empty] | 16 | [27 empty] | 16 | [25 empty] | 0 | 0 | 16 | 86 | 86 | 103 | 54 | 86 |  | 55.9 | 30.1 | 0.65 | 0.35
17 | 55 | 60 | 78 | 91 | 101 | 101 | 100 | 90 | 100 | 92 | 91 | 94 | 96 | 102 | 103 | 104 | 105 | 103 | 91 | 77 | 77 | 70 | 66 | 52 | 87 | 105 | 52 | 87 | 87.75 | 87.1667 | 87 | 17 | [28 empty] | 17 | [27 empty] | 17 | [25 empty] | 0 | 0 | 17 | 87 | 87 | 105 | 52 | 87 |  | 56.55 | 30.45 | 0.65 | 0.35
18 | 49 | 59 | 80 | 86 | 91 | 92 | 93 | 93 | 95 | 92 | 93 | 91 | 92 | 92 | 95 | 95 | 95 | 95 | 92 | 84 | 78 | 73 | 56 | 44 | 84 | 95 | 44 | 84 | 84.5 | 82.5833 | 84 | 18 | [28 empty] | 18 | [27 empty] | 18 | [25 empty] | 0 | 0 | 18 | 84 | 84 | 95 | 44 | 84 |  | 54.6 | 29.4 | 0.65 | 0.35
19 | 44 | 45 | 52 | 68 | 80 | 94 | 98 | 105 | 110 | 109 | 110 | 106 | 102 | 102 | 102 | 110 | 110 | 98 | 78 | 78 | 76 | 76 | 72 | 69 | 87 | 110 | 44 | 87 | 85.0833 | 89.4167 | 87 | 19 | [28 empty] | 19 | [27 empty] | 19 | [25 empty] | 0 | 0 | 19 | 87 | 87 | 110 | 44 | 87 |  | 56.55 | 30.45 | 0.65 | 0.35
20 | 45 | 42 | 49 | 61 | 84 | 100 | 102 | 118 | 112 | 113 | 111 | 110 | 104 | 105 | 105 | 106 | 104 | 108 | 117 | 105 | 103 | 86 | 84 | 81 | 94 | 118 | 42 | 94 | 87.25 | 100.6667 | 94 | 20 | [28 empty] | 20 | [27 empty] | 20 | [25 empty] | 0 | 0 | 20 | 94 | 94 | 118 | 42 | 94 |  | 61.1 | 32.9 | 0.65 | 0.35
21 | 90 | 102 | 104 | 112 | 115 | 120 | 121 | 121 | 105 | 107 | 110 | 105 | 105 | 96 | 95 | 99 | 100 | 105 | 105 | 99 | 93 | 72 | 64 | 50 | 100 | 121 | 50 | 94 | 109.3333 | 90.25 | 100 | 21 | [28 empty] | 21 | [27 empty] | 21 | [25 empty] | 0 | 0 | 21 | 100 | 94 | 121 | 50 | 100 |  | 65 | 35 | 0.65 | 0.35
22 | 51 | 63 | 72 | 113 | 120 | 101 | 106 | 105 | 149 | 148 | 118 | 111 | 101 | 72 | 85 | 102 | 107 | 105 | 97 | 85 | 65 | 59 | 56 | 49 | 93 | 149 | 49 | 93 | 104.75 | 81.9167 | 93 | 22 | [28 empty] | 22 | [27 empty] | 22 | [25 empty] | 0 | 0 | 22 | 93 | 93 | 149 | 49 | 93 |  | 60.45 | 32.55 | 0.65 | 0.35
23 | 66 | 78 | 82 | 113 | 97 | 99 | 101 | 96 | 98 | 107 | 103 | 104 | 105 | 100 | 98 | 100 | 101 | 99 | 100 | 95 | 87 | 81 | 68 | 57 | 93 | 113 | 57 | 93 | 95.3333 | 90.9167 | 93 | 23 | [28 empty] | 23 | [27 empty] | 23 | [25 empty] | 0 | 0 | 23 | 93 | 93 | 113 | 57 | 93 |  | 60.45 | 32.55 | 0.65 | 0.35
24 | 49 | 53 | 74 | 77 | 80 | 101 | 103 | 105 | 99 | 79 | 90 | 95 | 90 | 93 | 95 | 94 | 95 | 97 | 96 | 93 | 77 | 65 | 61 | 48 | 84 | 105 | 48 | 84 | 83.75 | 83.6667 | 84 | 24 | [28 empty] | 24 | [27 empty] | 24 | [25 empty] | 0 | 0 | 24 | 84 | 84 | 105 | 48 | 84 |  | 54.6 | 29.4 | 0.65 | 0.35
25 | 49 | 51 | 70 | 84 | 89 | 97 | 85 | 116 | 136 | 126 | 121 | 111 | 91 | 88 | 90 | 91 | 95 | 120 | 86 | 49 | 43 | 36 | 64 | 61 | 85 | 136 | 36 | 84 | 94.5833 | 76.1667 | 85 | 25 | [28 empty] | 25 | [27 empty] | 25 | [25 empty] | 0 | 0 | 25 | 85 | 84 | 136 | 36 | 85 |  | 55.25 | 29.75 | 0.65 | 0.35
26 | 61 | 55 | 60 | 56 | 60 | 102 | 106 | 108 | 107 | 107 | 95 | 90 | 92 | 93 | 94 | 94 | 93 | 93 | 76 | 76 | 74 | 71 | 67 | 68 | 83 | 108 | 55 | 83 | 83.9167 | 82.5833 | 83 | 26 | [28 empty] | 26 | [27 empty] | 26 | [25 empty] | 0 | 0 | 26 | 83 | 83 | 108 | 55 | 83 |  | 53.95 | 29.05 | 0.65 | 0.35
27 | 64 | 61 | 60 | 65 | 77 | 86 | 97 | 106 | 109 | 109 | 104 | 98 | 98 | 93 | 83 | 79 | 73 | 92 | 92 | 88 | 85 | 79 | 72 | 71 | 85 | 109 | 60 | 85 | 86.3333 | 83.75 | 85 | 27 | [28 empty] | 27 | [27 empty] | 27 | [25 empty] | 0 | 0 | 27 | 85 | 85 | 109 | 60 | 85 |  | 55.25 | 29.75 | 0.65 | 0.35
28 | 105 | 185 | 193 | 200 | 200 | 194 | 191 | 189 | 193 | 179 | 168 | 153 | 128 | 90 | 91 | 95 | 92 | 85 | 83 | 79 | 73 | 69 | 66 | 53 | 131 | 200 | 53 | 85 | 179.1667 | 83.6667 | 131 | 28 | [28 empty] | 28 | [27 empty] | 28 | [25 empty] | 0 | 0 | 28 | 131 | 85 | 200 | 53 | 131 |  | 85.15 | 45.85 | 0.65 | 0.35
29 | 57 | 82 | 90 | 91 | 92 | 93 | 93 | 91 | 91 | 91 | 88 | 88 | 88 | 89 | 90 | 92 | 94 | 77 | 76 | 68 | 68 | 64 | 61 | 64 | 82 | 94 | 57 | 82 | 87.25 | 77.5833 | 82 | 29 | [28 empty] | 29 | [27 empty] | 29 | [25 empty] | 0 | 0 | 29 | 82 | 82 | 94 | 57 | 82 |  | 53.3 | 28.7 | 0.65 | 0.35
30 | 64 | 67 | 69 | 73 | 85 | 105 | 103 | 100 | 97 | 94 | 94 | 90 | 86 | 87 | 92 | 94 | 95 | 92 | 77 | 75 | 72 | 69 | 55 | 54 | 83 | 105 | 54 | 83 | 86.75 | 79 | 83 | 30 | [28 empty] | 30 | [27 empty] | 30 | [25 empty] | 0 | 0 | 30 | 83 | 83 | 105 | 54 | 83 |  | 53.95 | 29.05 | 0.65 | 0.35
31 | 54 | 65 | 76 | 78 | 81 | 99 | 99 | 97 | 95 | 92 | 89 | 90 | 87 | 88 | 91 | 95 | 94 | 94 | 93 | 87 | 68 | 54 | 50 | 51 | 82 | 99 | 50 | 82 | 84.5833 | 79.3333 | 82 | 31 | [28 empty] | 31 | [27 empty] | 31 | [25 empty] | 0 | 0 | 31 | 82 | 82 | 99 | 50 | 82 |  | 53.3 | 28.7 | 0.65 | 0.35
AVG | 64 | 74 | 84 | 96 | 101 | 105 | 106 | 105 | 108 | 108 | 105 | 101 | 99 | 97 | 98 | 101 | 100 | 99 | 90 | 83 | 75 | 68 | 64 | 61 | 91 | 236 | 32 | 87 | 2986.4167 | 2670.1288 | 2827 | Average | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 0 |  | Average | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | 0 | AVG | #DIV/0! | #DIV/0! | #DIV/0! | 11 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 11 | 11 | 11 | Total | 2828 | 2701 | 236 | 32 | 2827 | 11 | 1838 | 990
2.0 STD | 50 | 64 | 62 | 74 | 63 | 51 | 44 | 41 | 47 | 47 | 42 | 35 | 29 | 27 | 18 | 18 | 19 | 20 | 26 | 28 | 26 | 27 | 28 | 43 | Avg | Max | Min | Dry | 97 | 86 | 92 | 2.0 STD | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  |  |  | 2.0 STD | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  |  | 2.0 STD | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  |  | Average | 91 | 87 | MAX | MIN | 91 | 11 | 59 | 32 | 65% | 35%
PLUS 2.0 STD | 114 | 138 | 146 | 170 | 164 | 156 | 150 | 146 | 155 | 154 | 146 | 136 | 128 | 124 | 116 | 119 | 118 | 119 | 116 | 110 | 102 | 95 | 92 | 103 | [7 empty] | Plus 2.0 STD | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 |  | Plus 2.0 STD | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 0 | 0 | PLUS 2.0 STD | #DIV/0! | #DIV/0! | #DIV/0! | 11 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 11 |  |  | MAXIMUM DAILY FLOW (MGD) |  |  | 136
[32 empty] | Avg Dry Flow | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Avg | Max | Min |  | Avg Dry Flow | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | MAX | MIN | AVG DRY FLOW | #DIV/0! | #DIV/0! | #DIV/0! | 11 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | MAX | MIN | MAXIMUM HOURLY FLOW (MGD)) |  |  | 236
Flows were taken from DCS | [31 empty] | Plus 2.0 STD | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  |  |  | Plus 2.0 STD | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  |  | PLUS 2.0 STD | #DIV/0! | #DIV/0! | #DIV/0! | 11 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Changed to Day time saving
BOWERY BAY -- DRY FLOW | [15 empty] | 2016-03-01 |  |  | 2016 | [12 empty] | Bowery Bay -- Dry Flow Calculation Sheet | [15 empty] | 2016-03-01 |  |  | 2016
SPDES PERMIT# NY0026158 | [31 empty] | Rain Flows are omitted here!
| AM |  |  |  | AM | Noon | PM | [9 empty] | PM | Midnt | AM | [13 empty] | AM |  |  |  | AM | Noon | PM | [9 empty] | PM | Midnt | AM
DATE | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | AVG | [6 empty] | DATE | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | AVG | MAX | MIN
1 | 60 | 78 | 95 | 96 | 96 | 95 | 94 | 87 | 87 | 85 | 87 | 75 | 65 | 68 | 98 | 111 | 112 | 109 | 104 | 91 | 88 | 67 | 62 | 57 | 86 | [6 empty] | 1 | 60 | 78 | 95 | 96 | 96 | 95 | 94 | 87 | 87 | 85 | 87 | 75 | 65 | 68 | 98 | 111 | 112 | 109 | 104 | 91 | 88 |  |  |  | 90 | 112 | 60 | Rain
2 | 58 | 66 | 76 | 85 | 111 | 101 | 102 | 74 | 75 | 76 | 78 | 74 | 86 | 111 | 107 | 107 | 108 | 105 | 102 | 98 | 73 | 60 | 47 | 48 | 85 | [6 empty] | 2 | [5 empty] | 101 | 102 | 74 | 75 | 76 | 78 | 74 | 86 | 111 | 107 | 107 | 108 | 105 | 102 | 98 | 73 | 60 | 47 | 48 | 86 | 111 | 47 | Rain
3 | 48 | 57 | 77 | 83 | 92 | 93 | 94 | 94 | 94 | 93 | 95 | 94 | 95 | 94 | 96 | 96 | 97 | 96 | 86 | 74 | 66 | 60 | 52 | 52 | 82 | [6 empty] | 3 | 48 | 57 | 77 | 83 | 92 | 93 | 94 | 94 | 94 | 93 | 95 | 94 | 95 | 94 | 96 | 96 | 97 | 96 | 86 | 74 | 66 | 60 | 52 | 52 | 82 | 97 | 48 | Clear
4 | 56 | 86 | 105 | 104 | 102 | 97 | 101 | 111 | 101 | 101 | 99 | 115 | 99 | 100 | 101 | 101 | 95 | 84 | 83 | 80 | 77 | 75 | 55 | 43 | 90 | [6 empty] | 4 | 56 | 86 | 105 | 104 | 102 | 97 | 101 | 111 |  |  |  | 115 | 99 | 100 | 101 | 101 | 95 | 84 | 83 | 80 | 77 | 75 | 55 | 43 | 89 | 115 | 43 | Snow
5 | 42 | 44 | 51 | 63 | 84 | 100 | 108 | 108 | 108 | 108 | 108 | 107 | 102 | 102 | 102 | 103 | 101 | 88 | 85 | 84 | 81 | 78 | 72 | 45 | 86 | [6 empty] | 5 | 42 | 44 | 51 | 63 | 84 | 100 | 108 | 108 | 108 | 108 | 108 | 107 | 102 | 102 | 102 | 103 | 101 | 88 | 85 | 84 | 81 | 78 | 72 | 45 | 86 | 108 | 42 | Clear
6 | 44 | 55 | 60 | 86 | 94 | 95 | 97 | 99 | 99 | 101 | 103 | 105 | 108 | 98 | 90 | 93 | 96 | 96 | 93 | 87 | 76 | 69 | 61 | 59 | 86 | [6 empty] | 6 | 44 | 55 | 60 | 86 | 94 | 95 | 97 | 99 | 99 | 101 | 103 | 105 | 108 | 98 | 90 | 93 | 96 | 96 | 93 | 87 | 76 | 69 | 61 | 59 | 86 | 108 | 44 | Clear
7 | 59 | 88 | 95 | 97 | 104 | 106 | 104 | 98 | 97 | 101 | 87 | 89 | 91 | 99 | 104 | 110 | 105 | 101 | 67 | 59 | 45 | 41 | 38 | 32 | 84 | [6 empty] | 7 | 59 | 88 | 95 | 97 | 104 | 106 | 104 | 98 | 97 | 101 | 87 | 89 | 91 | 99 | 104 | 110 | 105 | 101 | 67 | 59 | 45 | 41 | 38 | 32 | 84 | 110 | 32 | Clear
8 | 77 | 99 | 100 | 98 | 98 | 97 | 96 | 95 | 92 | 86 | 88 | 89 | 90 | 92 | 93 | 96 | 94 | 94 | 83 | 78 | 77 | 73 | 54 | 53 | 87 | [6 empty] | 8 | 77 | 99 | 100 | 98 | 98 | 97 | 96 | 95 | 92 | 86 | 88 | 89 | 90 | 92 | 93 | 96 | 94 | 94 | 83 | 78 | 77 | 73 | 54 | 53 | 87 | 100 | 53 | Clear
9 | 54 | 59 | 78 | 93 | 92 | 95 | 109 | 105 | 109 | 112 | 86 | 88 | 104 | 108 | 110 | 107 | 105 | 107 | 85 | 85 | 81 | 78 | 72 | 81 | 92 | [6 empty] | 9 | 54 | 59 | 78 | 93 | 92 | 95 | 109 | 105 | 109 | 112 | 86 | 88 | 104 | 108 | 110 | 107 | 105 | 107 | 85 | 85 | 81 | 78 | 72 | 81 | 92 | 112 | 54 | Clear
10 | 80 | 74 | 85 | 64 | 81 | 84 | 89 | 96 | 111 | 106 | 100 | 103 | 95 | 94 | 93 | 99 | 100 | 100 | 100 | 89 | 78 | 75 | 81 | 81 | 90 | [6 empty] | 10 | 80 | 74 | 85 | 64 | 81 | 84 | 89 | 96 | 111 | 106 | 100 | 103 | 95 | 94 | 93 | 99 | 100 | 100 | 100 | 89 | 78 | 75 | 81 | 81 | 90 | 111 | 64 | Clear
11 | 81 | 85 | 93 | 97 | 102 | 101 | 102 | 100 | 99 | 98 | 98 | 98 | 98 | 98 | 98 | 99 | 89 | 89 | 81 | 73 | 71 | 64 | 54 | 47 | 88 | [6 empty] | 11 | 81 | 85 | 93 | 97 | 102 | 101 | 102 | 100 | 99 | 98 | 98 | 98 | 98 | 98 | 98 | 99 | 89 | 89 | 81 | 73 | 71 | 64 | 54 | 47 | 88 | 102 | 47 | Rain
12 | 44 | 44 | 50 | 74 | 95 | 98 | 101 | 103 | 103 | 104 | 104 | 104 | 104 | 103 | 102 | 101 | 100 | 96 | 87 |  | 84 | 76 | 62 | 59 | 87 | [6 empty] | 12 | 44 | 44 | 50 | 74 | 95 | 98 | 101 | 103 | 103 | 104 | 104 | 104 | 104 | 103 | 102 | 101 | 100 | 96 | 87 |  | 84 | 76 | 62 | 59 | 87 | 104 | 44 | Clear
13 | 51 | 50 | 58 | 74 | 77 | 82 | 93 | 103 | 103 | 104 | 106 | 104 | 103 | 103 | 103 | 105 | 103 | 102 | 101 | 90 | 79 | 74 | 65 | 44 | 87 | [6 empty] | 13 | 51 | 50 | 58 | 74 | 77 | 82 | 93 | 103 | 103 | 104 | 106 | 104 | 103 | 103 | 103 | 105 | 103 | 102 | 101 | 90 | 79 | 74 | 65 | 44 | 87 | 106 | 44 | Clear
14 | 46 | 59 | 76 | 85 | 92 | 98 | 100 | 100 | 101 | 101 | 99 | 98 | 96 | 96 | 97 | 100 | 99 | 98 | 89 | 82 | 97 | 83 | 67 | 69 | 89 | [6 empty] | 14 | 46 | 59 | [18 empty] | 97 | 83 | 67 | 69 | 70 | 97 | 46 | Rain
15 | 87 | 115 | 123 | 123 | 121 | 116 | 110 | 95 | 94 | 108 | 122 | 118 | 120 | 115 | 102 | 107 | 104 | 93 | 59 | 51 | 44 | 33 | 57 | 82 | 96 | [6 empty] | 15 | 87 | 115 | 123 | 123 | 121 | 116 | 110 | 95 | 94 | 108 | 122 | 118 | 120 | 115 | 102 | 107 | 104 | 93 | 59 | 51 | 44 | 33 | 57 | 82 | 96 | 123 | 33 | Clear
16 | 78 | 62 | 62 | 87 | 103 | 101 | 101 | 99 | 98 | 95 | 91 | 82 | 85 | 90 | 96 | 101 | 102 | 102 | 99 | 92 | 70 | 58 | 55 | 54 | 86 | [6 empty] | 16 | 78 | 62 | 62 | 87 | 103 | 101 | 101 | 99 | 98 | 95 | 91 | 82 | 85 | 90 | 96 | 101 | 102 | 102 | 99 | 92 | 70 | 58 | 55 | 54 | 86 | 103 | 54 | Rain
17 | 55 | 60 | 78 | 91 | 101 | 101 | 100 | 90 | 100 | 92 | 91 | 94 | 96 | 102 | 103 | 104 | 105 | 103 | 91 | 77 | 77 | 70 | 66 | 52 | 87 | [6 empty] | 17 | 55 | 60 | 78 | 91 | 101 | 101 | 100 | 90 | 100 | 92 | 91 | 94 | 96 | 102 | 103 | 104 | 105 | 103 | 91 | 77 | 77 | 70 | 66 | 52 | 87 | 105 | 52 | Clear
18 | 49 | 59 | 80 | 86 | 91 | 92 | 93 | 93 | 95 | 92 | 93 | 91 | 92 | 92 | 95 | 95 | 95 | 95 | 92 | 84 | 78 | 73 | 56 | 44 | 84 | [6 empty] | 18 | 49 | 59 | 80 | 86 | 91 | 92 | 93 | 93 | 95 | 92 | 93 | 91 | 92 | 92 | 95 | 95 | 95 | 95 | 92 | 84 | 78 | 73 | 56 | 44 | 84 | 95 | 44 | Clear
19 | 44 | 45 | 52 | 68 | 80 | 94 | 98 | 105 | 110 | 109 | 110 | 106 | 102 | 102 | 102 | 110 | 110 | 98 | 78 | 78 | 76 | 76 | 72 | 69 | 87 | [6 empty] | 19 | 44 | 45 | 52 | 68 | 80 | 94 | 98 | 105 | 110 | 109 | 110 | 106 | 102 | 102 | 102 | 110 | 110 | 98 | 78 | 78 | 76 | 76 | 72 | 69 | 87 | 110 | 44 | Clear
20 | 45 | 42 | 49 | 61 | 84 | 100 | 102 | 118 | 112 | 113 | 111 | 110 | 104 | 105 | 105 | 106 | 104 | 108 | 117 | 105 | 103 | 86 | 84 | 81 | 94 | [6 empty] | 20 | 45 | 42 | 49 | 61 | 84 | 100 | 102 | 118 | 112 | 113 | 111 | 110 | 104 | 105 | 105 | 106 | 104 | 108 | 117 | 105 | 103 | 86 | 84 | 81 | 94 | 118 | 42 | Snow
21 | 58 | 66 | 104 | 112 | 115 | 98 | 100 | 100 | 105 | 107 | 110 | 105 | 105 | 96 | 95 | 99 | 100 | 105 | 105 | 99 | 93 | 72 | 64 | 50 | 94 | [6 empty] | 21 | [8 empty] | 105 | 107 | 110 | 105 | 105 | 96 | 95 | 99 | 100 | 105 | 105 | 99 | 93 | 72 | 64 | 50 | 94 | 110 | 50 | Snow/Clear
22 | 51 | 63 | 72 | 113 | 120 | 101 | 106 | 105 | 149 | 148 | 118 | 111 | 101 | 72 | 85 | 102 | 107 | 105 | 97 | 85 | 65 | 59 | 56 | 49 | 93 | [6 empty] | 22 | 51 | 63 | 72 | 113 | 120 | 101 | 106 | 105 | 149 | 148 | 118 | 111 | 101 | 72 | 85 | 102 | 107 | 105 | 97 | 85 | 65 | 59 | 56 | 49 | 93 | 149 | 49 | Clear
23 | 66 | 78 | 82 | 113 | 97 | 99 | 101 | 96 | 98 | 107 | 103 | 104 | 105 | 100 | 98 | 100 | 101 | 99 | 100 | 95 | 87 | 81 | 68 | 57 | 93 | [6 empty] | 23 | 66 | 78 | 82 | 113 | 97 | 99 | 101 | 96 | 98 | 107 | 103 | 104 | 105 | 100 | 98 | 100 | 101 | 99 | 100 | 95 | 87 | 81 | 68 | 57 | 93 | 113 | 57 | Clear
24 | 49 | 53 | 74 | 77 | 80 | 101 | 103 | 105 | 99 | 79 | 90 | 95 | 90 | 93 | 95 | 94 | 95 | 97 | 96 | 93 | 77 | 65 | 61 | 48 | 84 | [6 empty] | 24 | 49 | 53 | 74 | 77 | 80 | 101 | 103 | 105 | 99 | 79 | 90 | 95 | 90 | 93 | 95 | 94 | 95 | 97 | 96 | 93 | 77 | 65 | 61 | 48 | 84 | 105 | 48 | Clear
25 | 49 | 51 | 70 | 84 | 89 | 97 | 85 | 116 | 101 | 126 | 121 | 111 | 91 | 88 | 90 | 91 | 95 | 120 | 86 | 49 | 43 | 36 | 64 | 61 | 84 | [6 empty] | 25 | 49 | 51 | 70 | 84 | 89 | 97 | 85 | 116 |  |  | 121 | 111 | 91 | 88 | 90 | 91 | 95 | 120 | 86 | 49 | 43 | 36 | 64 | 61 | 81 | 121 | 36 | Rain
26 | 61 | 55 | 60 | 56 | 60 | 102 | 106 | 108 | 107 | 107 | 95 | 90 | 92 | 93 | 94 | 94 | 93 | 93 | 76 | 76 | 74 | 71 | 67 | 68 | 83 | [6 empty] | 26 | 61 | 55 | 60 | 56 | 60 | 102 | 106 | 108 | 107 | 107 | 95 | 90 | 92 | 93 | 94 | 94 | 93 | 93 | 76 | 76 | 74 | 71 | 67 | 68 | 83 | 108 | 55 | Clear
27 | 64 | 61 | 60 | 65 | 77 | 86 | 97 | 106 | 109 | 109 | 104 | 98 | 98 | 93 | 83 | 79 | 73 | 92 | 92 | 88 | 85 | 79 | 72 | 71 | 85 | [6 empty] | 27 | 64 | 61 | 60 | 65 | 77 | 86 | 97 | 106 | 109 | 109 | 104 | 98 | 98 | 93 | 83 | 79 | 73 | 92 | 92 | 88 | 85 | 79 | 72 | 71 | 85 | 109 | 60 | Clear
28 | 58 | 66 | 76 | 85 | 92 | 98 | 100 | 100 | 101 | 101 | 99 | 98 | 96 | 90 | 91 | 95 | 92 | 85 | 83 | 79 | 73 | 69 | 66 | 53 | 85 | [6 empty] | 28 | [13 empty] | 90 | 91 | 95 | 92 | 85 | 83 | 79 | 73 | 69 | 66 | 53 | 80 | 95 | 53 | Rain
29 | 57 | 82 | 90 | 91 | 92 | 93 | 93 | 91 | 91 | 91 | 88 | 88 | 88 | 89 | 90 | 92 | 94 | 77 | 76 | 68 | 68 | 64 | 61 | 64 | 82 | [6 empty] | 29 | 57 | 82 | 90 | 91 | 92 | 93 | 93 | 91 | 91 | 91 | 88 | 88 | 88 | 89 | 90 | 92 | 94 | 77 | 76 | 68 | 68 | 64 | 61 | 64 | 82 | 94 | 57 | Clear
30 | 64 | 67 | 69 | 73 | 85 | 105 | 103 | 100 | 97 | 94 | 94 | 90 | 86 | 87 | 92 | 94 | 95 | 92 | 77 | 75 | 72 | 69 | 55 | 54 | 83 | [6 empty] | 30 | 64 | 67 | 69 | 73 | 85 | 105 | 103 | 100 | 97 | 94 | 94 | 90 | 86 | 87 | 92 | 94 | 95 | 92 | 77 | 75 | 72 | 69 | 55 | 54 | 83 | 105 | 54 | Clear
31 | 54 | 65 | 76 | 78 | 81 | 99 | 99 | 97 | 95 | 92 | 89 | 90 | 87 | 88 | 91 | 95 | 94 | 94 | 93 | 87 | 68 | 54 | 50 | 51 | 82 | [6 empty] | 31 | 54 | 65 | 76 | 78 | 81 | 99 | 99 | 97 | 95 | 92 | 89 | 90 | 87 | 88 | 91 | 95 | 94 | 94 | 93 | 87 | 68 | 54 | 50 | 51 | 82 | 99 | 50 | Clear
Total | 1789 | 2034 | 2376 | 2662 | 2888 | 3025 | 3087 | 3097 | 3140 | 3146 | 3067 | 3024 | 2974 | 2961 | 3001 | 3086 | 3063 | 3023 | 2763 | 2451 | 2326 | 2088 | 1916 | 1778 | 2701 | [6 empty] | Average | 58 | 66 | 76 | 85 | 92 | 98 | 100 | 100 | 101 | 101 | 99 | 98 | 96 | 96 | 97 | 100 | 99 | 98 | 89 | 82 | 75 | 67 | 62 | 57 | 2678 | 3355 | 1506
Average | 58 | 66 | 77 | 86 | 93 | 98 | 100 | 100 | 101 | 101 | 99 | 98 | 96 | 96 | 97 | 100 | 99 | 98 | 89 | 82 | 75 | 67 | 62 | 57 | 87 | [6 empty] | 2.0 STD | 25 | 35 | 36 | 34 | 26 | 13 | 12 | 18 | 25 | 27 | 22 | 22 | 20 | 19 | 13 | 14 | 15 | 17 | 24 | 26 | 26 | 26 | 19 | 25
[32 empty] | Plus 2.0 STD | 83 | 100 | 112 | 119 | 117 | 111 | 111 | 118 | 126 | 128 | 121 | 120 | 116 | 115 | 110 | 113 | 114 | 114 | 113 | 108 | 102 | 93 | 81 | 83 | 86 | 149 | 32
[32 empty] | Avg Dry Flow | 58 | 66 | 76 | 85 | 92 | 98 | 100 | 100 | 101 | 101 | 99 | 98 | 96 | 96 | 97 | 100 | 99 | 98 | 89 | 82 | 75 | 67 | 62 | 57 | Avg | Max | Min
[32 empty] | Plus 2.0 STD | 83 | 100 | 112 | 119 | 117 | 111 | 111 | 118 | 126 | 128 | 121 | 120 | 116 | 115 | 110 | 113 | 114 | 114 | 113 | 108 | 102 | 93 | 81 | 83
[33 empty] | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00
1
2
3
4
5
6
7
8
9
10
11
[32 empty] | 12 | [19 empty] | !!!
13
14
[32 empty] | 15 | !!! | !!! | !!! | !!! | !!! | !!! |  |  |  |  | !!! |  | !!!
16
17
18
19
[32 empty] | 20 | [18 empty] | !!! |  | !!! |  | !!!
21
[32 empty] | 22 |  |  |  |  | !!! |  |  |  | !!! | !!!
23
24
[32 empty] | 25 | [17 empty] | !!!
26
27
28
29
30
31

## DW_
| Bowery Bay WPCP Dewatering Sheet | [6 empty] | 2016-03-01 |  | 2016 |  |  | Bowery Bay WPCP Dewatering Sheet | [18 empty] | 2016-03-01 |  | 2016 |  |  | Bowery Bay WPCP Dewatering Sheet | [9 empty] | 2016-03-01 |  | 2016
| Sludge |  | Cake |  | Centrifuge |  | Centrate | [5 empty] | Centrifuges |  | Sludge Feed |  |  | centrate |  | Polymer: | 41% | active | Mixed Conc. |  | #DIV/0! | Centrifuge |  | Cake Removed |  |  | Centrate | [5 empty] | Ferric | Odor Control |  | Power (KWH) |  | Building Heating
D | Feed |  | Total | Total | Sludge Feed Rate gpm | Loading Rate DT/Hr | SS | VOL. | cBOD | ALK | D | D | Units | Oper |  |  |  | gallons by totalizer | flow @ 95% of sludge feed |  | 8.67 | [lbs/gal] | Neat Conc. |  | #DIV/0! | % | Truck | Wet | Dry |  | Flow | TS | SS | CBOD | D | D | Chloride | Hypo | NaOH |  | /Wet | Fuel Oil | Purchased | Digester | D
A | To Centrifuges |  | Solids | Vol Sol |  |  |  | SS |  |  | A | A | In | Hours | Gallons | Cu. Ft. | Dry |  |  | Gal From | GPM | Gal Mix | Active | Act. Lbs/ | lbs of poly/ | Capture | Trips | Tons | Tons | Cu. Ft. | MGD | LBS/ | LBS/ | LBS/ | A | A | Gal | Gal | Gal | Total | Ton | Gal | Gas | Gas | A
Y | %SOL | %VOL | % | % |  |  | mg/L | % | mg/L | mg/L | Y | Y | Operation |  |  |  | Tons |  |  | Storage |  | Polymer | Lbs | Dry Ton | Dry Ton | [6 empty] | DAY | DAY | DAY | Y | Y | [6 empty] | 1000 Cu. Ft. | 1000 Cu. Ft. | Y
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 |  |  | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 |  |  | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40
1 | [10 empty] | 1 | 1 | [22 empty] | 1 | 1 | 0 | [6 empty] | N | 1 | Dewatered Sludge Cake Inventory And Production
2 | [10 empty] | 2 | 2 | [22 empty] | 2 | 2 | 0 | [7 empty] | 2
3 | [10 empty] | 3 | 3 | [22 empty] | 3 | 3 | 0 | [6 empty] | O | 3 | Dry Tons Cake Inventory 1st of Month |  |  | = | 0
4 | [10 empty] | 4 | 4 | [22 empty] | 4 | 4 | 0 | [7 empty] | 4 | Dry Tons Cake Inventory End of Month |  |  | = | 0
5 | [10 empty] | 5 | 5 | [22 empty] | 5 | 5 | 0 | [7 empty] | 5 | Dry Tons Cake Removed for Month |  |  | = | 0
6 | [10 empty] | 6 | 6 | [22 empty] | 6 | 6 | 0 | [6 empty] | M | 6 | Dry Tons Cake Produced for Month |  |  | = | 0
7 | [10 empty] | 7 | 7 | [22 empty] | 7 | 7 | 0 | [7 empty] | 7 | % Capture |  |  | = | #DIV/0!
8 | [10 empty] | 8 | 8 | [22 empty] | 8 | 8 | 0 | [6 empty] | E | 8
9 | [10 empty] | 9 | 9 | [22 empty] | 9 | 9 | 0 | [7 empty] | 9 | % Capture is calculated as follows:
10 | [10 empty] | 10 | 10 | [22 empty] | 10 | 10 | 0 | [6 empty] | T | 10 | 1-((dry tons feed-dry tons produced)/dry tons feed)
11 | [10 empty] | 11 | 11 | [22 empty] | 11 | 11 | 0 | [7 empty] | 11
12 | [10 empty] | 12 | 12 | [22 empty] | 12 | 12 | 0 | [6 empty] | E | 12
13 | [10 empty] | 13 | 13 | [22 empty] | 13 | 13 | 0 | [7 empty] | 13
14 | [10 empty] | 14 | 14 | [22 empty] | 14 | 14 | 0 | [6 empty] | R | 14
15 | [10 empty] | 15 | 15 | [22 empty] | 15 | 15 | 0 | [7 empty] | 15
16 | [10 empty] | 16 | 16 | [22 empty] | 16 | 16 | 0 | [6 empty] | S | 16
17 | [10 empty] | 17 | 17 | [22 empty] | 17 | 17 | 0 | [7 empty] | 17
18 | [10 empty] | 18 | 18 | [22 empty] | 18 | 18 | 0 | [7 empty] | 18
19 | [10 empty] | 19 | 19 | [22 empty] | 19 | 19 | 0 | [7 empty] | 19
20 | [10 empty] | 20 | 20 | [22 empty] | 20 | 20 | 0 | [7 empty] | 20
21 | [10 empty] | 21 | 21 | [22 empty] | 21 | 21 | 0 | [7 empty] | 21
22 | [10 empty] | 22 | 22 | [22 empty] | 22 | 22 | 0 | [7 empty] | 22
23 | [10 empty] | 23 | 23 | [22 empty] | 23 | 23 | 0 | [7 empty] | 23
24 | [10 empty] | 24 | 24 | [22 empty] | 24 | 24 | 0 | [7 empty] | 24
25 | [10 empty] | 25 | 25 | [22 empty] | 25 | 25 | 0 | [7 empty] | 25
26 | [10 empty] | 26 | 26 | [22 empty] | 26 | 26 | 0 | [7 empty] | 26
27 | [10 empty] | 27 | 27 | [22 empty] | 27 | 27 | 0 | [7 empty] | 27
28 | [10 empty] | 28 | 28 | [22 empty] | 28 | 28 | 0 | [7 empty] | 28
29 | [10 empty] | 29 | 29 | [22 empty] | 29 | 29 | 0 | [7 empty] | 29
30 | [10 empty] | 30 | 30 | [22 empty] | 30 | 30 | 0 | [7 empty] | 30
31 | [10 empty] | 31 | 31 | [22 empty] | 31 | 31 | 0 | [7 empty] | 31
AVG | [10 empty] | AVG | Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | Total | Total | [8 empty] | TOT
[12 empty] | Avg | [22 empty] | Avg | Avg | [8 empty] | AVG
| Dewatering shut down on 1/4/2016 for belt contract work | [11 empty] | Lbs 21: Contractual Comparison
[25 empty] | Actual | Contract | Pass?
[23 empty] | Dosage (lbs/ton) |  | #DIV/0! | 61.18 | #DIV/0!
[23 empty] | Centrate (mg/L) |  |  | 1200 | NO
[23 empty] | Cake (%Sol) |  | #VALUE! | 25% | #VALUE!
|  | DATE PRINTED: |  |  | 2016-05-16 13:11 | 42506.5493 |  |  | Page 1 of 3 |  |  |  | DAY 31: Page 2 of 3 | [13 empty] | Page 3 of 3
*Centrate totalizer is not reading correctly, the flow of centrate cannot be greater than sludge feed
Centrate totalizer OOS on 5/15/5015

## MASS
[27 empty] | BOWERY BAY: |  | INVENTORY |  | TOTALS |  | % MASS
BOWERY BAY FLOW AND MASS BALANCE | [6 empty] | 2016-03-01 |  |  | 2016 | [9 empty] | FLOWS USING MONTHLY TOTALS | [6 empty] | SLUDGE MASS BALANCE |  | CUFT | LBS | CUFT | LBS | BALANCE
[27 empty] | #REF! |  | x 1000 | x 1000 | x 1000 | x 1000 | ERROR
DATE PRINTED |  | 2016-05-16 13:11 | 42506.5493 | [17 empty] | R E C Y C L E | [5 empty] | TANK AND CENTRIFUGE INVENTORY/THROUGHPUT | [5 empty] | #VALUE!
[14 empty] | SECONDARY BYPASS | [12 empty] | BB: SLUDGE PRODUCTION |  |  |  |  | 0
[5 empty] | RECYCLES | [21 empty] | BB: SLUDGE TO OAKWOOD BEACH |  |  |  | 0 | 2055227
[5 empty] | FLOW: | 11.3694 | MGD |  | FLOW: | 11 | MGD | RAS | [5 empty] | TO SCUM COLLECTOR | [8 empty] | BB SLUDGE STORAGE: START OF MONTH
[5 empty] | CONC: | 680 | PPM |  | CONC: | 78.25 | PPM | FLOW: | 59.3065 | MASS: | 3190271.9516 | LBS/DAY |  | FLOW: | 0 | CU.FT./MONTH | [6 empty] | BB SLUDGE STORAGE: START OF MONTH
[5 empty] | MASS: | 64478.339 | LBS/DAY |  | MASS: | 7178.655 | LBS/DAY | CONC: | 6450 | PPM |  |  |  | CONC: | 60 | % | [6 empty] | BB SLUDGE STORAGE: END OF MONTH
[18 empty] | MASS: | 0 | D.LB/MONTH | [6 empty] | BB SLUDGE STORAGE: END OF MONTH
|  | MAIN SEWAGE |  |  |  | PRIMARY |  |  |  |  | AERATION |  |  |  |  | FINAL |  |  |  |  | CHLORINE | [5 empty] | SLUDGE TO CENTRIFUGE |  |  |  | 0 | 0
INFLUENT |  | PUMPS |  | RAW |  | TANKS |  |  | PRIM. EFF. |  | TANKS |  |  | MLSS |  | TANKS |  |  |  |  | CONTACT TANK |  |  | EFFLUENT |  |  | CENTRATE SOLIDS
FLOW: | 91 | MGD |  | FLOW: | 102.3694 | MGD |  |  | FLOW: | 102.3694 | MGD | SWAS |  | FLOW: | 150.5 |  | WAS | [6 empty] | FLOW: | 91 | MGD | CAKE TRUCKED |  |  |  |  | 0
CONC: | 149 | PPM |  | CONC: | 207.9743 | PPM |  |  | CONC: | 78.25 | PPM | FLOW: | 1.4916 | CONC: | 3000 |  | FLOW: | 0.8 | MGD |  |  |  |  | CONC: | 12 | PPM | CAKE IN HOPPERS: START OF MONTH |  | 0
MASS: | 113082.06 | LBS/DAY |  | MASS: | 177560.399 | LBS/DAY |  |  | MASS: | 66806.805 | LBS | CONC: | 6256.7771 | MASS: | 3765510 |  | CONC: | 6800 | PPM |  |  |  |  | MASS: | 9107.28 | LBS/DAY | CAKE IN STORAGE: START OF MONTH |  | 271.2166
| 56.541 | TONS/DAY | [9 empty] | MASS: | 77835.2647 | LBS/DAY |  |  | MASS: | 45369.6 | LBS/DAY | [7 empty] | CAKE IN HOPPERS: END OF MONTH |  | 0
[27 empty] | CAKE IN STORAGE: END OF MONTH |  | 359.4329
[7 empty] | PRIMARY SLUDGE. | [6 empty] | WASTE SLUDGE | [5 empty] | MASS IN - MASS OUT = ACC. | [6 empty] | BALANCE AROUND STORAGE TANKS | [5 empty] | 100
SLUDGE OUT | [6 empty] | FLOW: | 9.0778 | MGD |  |  |  |  | BOX | [12 empty] | SLUDGE TO STORAGE |  |  |  | #VALUE! | 2055227
FLOW: |  | CU.FT./DAY |  |  |  |  | CONC: | 1462.8867 | PPM |  |  |  | WASTE SL. TO THICK. | [6 empty] | MASS IN | 113082.06 | [5 empty] | CHANGE IN STORAGE |  | 0 | 0
%SOL: | [6 empty] | MASS: | 110753.594 | LBS/DAY |  |  |  | FLOW: | 11.3694 | MGD |  |  |  |  | MASS OUT | 149891.9574 |  | thicken sludge + effluent |  |  |  | SLUDGE FROM STORAGE TO CENTRIFUGES |  |  |  | 0 | 0
MASS: | #VALUE! | LBS/DAY | [10 empty] | CONC: | 2838.95 | ppm |  |  |  |  | ACC. | -36809.8974 | LBS/DAY | -4413.6568 | GAL./DAY |  |  | BALANCE AROUND CENTRIFUGES | [5 empty] | #VALUE!
| #VALUE! | TONS/DAY | [10 empty] | MASS: | 269192.3245 | LBS/DAY |  |  |  | % Mass Balance Error |  | -32.55% |  | -584.2841 | CU.FT./DAY |  |  | SLUDGE FROM STORAGE TO CENTRIFUGES |  |  |  | 0 | 0
|  | STORAGE |  | DIG.SL. OUT |  | DIGESTER |  | THICK SL. |  | THICKENER |  |  | THICKENERS FEED | [13 empty] | CHANGE IN CAKE STORAGE |  | 88.2163 | 0
|  | TANKS |  |  |  | TANKS |  |  |  | TANKS | [16 empty] | CENTRAGE SOLIDS
|  |  |  | FLOW: | 65725.8065 | CU.FT./DAY |  | FLOW: | 65725.8065 | CU.FT./DAY | THICK OVER FLOW | [15 empty] | HAULED SOLIDS |  |  |  |  | 0
|  |  |  | %SOL: | 1.9 |  |  | %SOL: | 3.4 |  | FLOW: | 11.3694 | MGD
|  |  |  | MASS: | 78673.7903 | LBS/DAY |  | MASS: | 140784.6774 | LBS/DAY | CONC: | 680 | PPM | [13 empty] | % Mass Balance Error % = (In-(Out+Storage Tank Inventory Accumulation))/In*100%.
[11 empty] | MASS: | 64478.339 | LBS | [13 empty] | Done around the total system (production/hauled/centrate), storage tanks, and centrifuges.
TOTAL SOLIDS FROM DEWATERING
|  | DEWATERING |  |  |  | %SOL: | [20 empty] | BOWERY BAY PERCENT SOLIDS: | 1.6
|  | CENTRIFUGES |  |  |  | MASS: | #VALUE! | LBS/DAY |  |  |  | 450.2778 | [14 empty] | BOWERY BAY PERCENT SOLIDS: | 2.2
|  |  | Centrate to AT10 |  |  | DT/DAY | #VALUE!
|  |  | FLOW: | 4.4858e-05 | MGD
|  |  | solids |  | ppm | DT/DAY |  | cake removed by trucks
|  |  | MASS: | 0 | LBS/DAY | [10 empty] | ACC. IS THE AMOUNT OF SLUDGE REMAINED IN THE SLUDGE STORAGE TANKS.
|  |  | DT/DAY | 0 | [11 empty] | % Mass Balance Error % = (In-(Out+Storage Tank Inventory Accumulation))/In*100%.
Done around the total system (production/hauled/centrate), storage tanks, and centrifuges.

## Grit
:wcs
Bowery Bay |  |  |  | TRANSPORTATION SECTION MVO | [22 empty] | PRIVATE CONTRACTORS
PLANT | [7 empty] | TRUCK TRIP | [34 empty] | CONTAINER WORKSHEET
2016-03-01 |  | GRIT |  |  |  |  | SCREEN | [5 empty] | MIXED |  |  |  |  | GREASE | [5 empty] | GRIT |  |  |  | SCREEN | [5 empty] | MIXED |  |  |  | GREASE | [10 empty] | MIXED
DATE | 6CY | 10CY | 15CY | 20CY | 26CY | 6CY | 10CY | 15CY | 20CY | 26CY | 6CY | 10CY | 15CY | 20CY | 26CY | 28CY | 6CY | 10CY | 15CY | 20CY | 26CY | 6CY | 10CY | 15CY | 20CY | 26CY | 6CY | 10CY | 15CY | 20CY | 26CY | 6CY | 10CY | 15CY | 20CY | 26CY | 28CY | 6CY | 10CY | 15CY | 20CY | 26CY | SCREENINGS |  | GRIT |  | GREASE |  | SCREEN
| 6 | 10 | 15 | 20 | 26 | 6 | 10 | 15 | 20 | 26 | 6 | 10 | 15 | 20 | 26 | 28 | 6 | 10 | 15 | 20 | 26 | 6 | 10 | 15 | 20 | 26 | 6 | 10 | 15 | 20 | 26 | 6 | 10 | 15 | 20 | 26 | 28 | 6 | 10 | 15 | 20 | 26 | CUYDS | CUFT | CUYDS | CUFT | CUYDS | CUFT | CUYDS | CUFT
2016-03-01 | [5 empty] | 1 | [36 empty] | 6 | 162 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-02 | [5 empty] | 1 | [36 empty] | 6 | 162 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-03 | 2 | [41 empty] | 0 | 0 | 12 | 324 | 0 | 0 | 0 | 0
2016-03-04 | 2 | [41 empty] | 0 | 0 | 12 | 324 | 0 | 0 | 0 | 0
2016-03-05 | [5 empty] | 1 | [36 empty] | 6 | 162 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-06 | 1 | [41 empty] | 0 | 0 | 6 | 162 | 0 | 0 | 0 | 0
2016-03-07 | 2 | [41 empty] | 0 | 0 | 12 | 324 | 0 | 0 | 0 | 0
2016-03-08 | 6 | [41 empty] | 0 | 0 | 36 | 972 | 0 | 0 | 0 | 0
2016-03-09 | [42 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-10 | 2 | [41 empty] | 0 | 0 | 12 | 324 | 0 | 0 | 0 | 0
2016-03-11 | 1 |  |  |  |  | 1 | [36 empty] | 6 | 162 | 6 | 162 | 0 | 0 | 0 | 0
2016-03-12 | 1 | [41 empty] | 0 | 0 | 6 | 162 | 0 | 0 | 0 | 0
2016-03-13 | [42 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-14 | 3 |  |  |  |  | 4 | 1 | [35 empty] | 34 | 918 | 18 | 486 | 0 | 0 | 0 | 0
2016-03-15 | 2 | [5 empty] | 1 | [35 empty] | 10 | 270 | 12 | 324 | 0 | 0 | 0 | 0
2016-03-16 | 2 |  |  |  |  | 1 | [36 empty] | 6 | 162 | 12 | 324 | 0 | 0 | 0 | 0
2016-03-17 | 1 |  |  |  |  | 2 | [36 empty] | 12 | 324 | 6 | 162 | 0 | 0 | 0 | 0
2016-03-18 | 1 | [41 empty] | 0 | 0 | 6 | 162 | 0 | 0 | 0 | 0
2016-03-19 | [42 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-20 | 1 |  |  |  |  | 1 | [36 empty] | 6 | 162 | 6 | 162 | 0 | 0 | 0 | 0
2016-03-21 | 3 | [41 empty] | 0 | 0 | 18 | 486 | 0 | 0 | 0 | 0
2016-03-22 | 2 | [41 empty] | 0 | 0 | 12 | 324 | 0 | 0 | 0 | 0
2016-03-23 | [5 empty] | 1 | [36 empty] | 6 | 162 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-24 | 1 |  |  |  |  | 1 | [36 empty] | 6 | 162 | 6 | 162 | 0 | 0 | 0 | 0
2016-03-25 | 1 |  |  |  |  | 1 | [36 empty] | 6 | 162 | 6 | 162 | 0 | 0 | 0 | 0
2016-03-26 | 1 |  |  |  |  | 3 | [36 empty] | 18 | 486 | 6 | 162 | 0 | 0 | 0 | 0
2016-03-27 | [42 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-28 | 2 |  |  |  |  | 2 | [36 empty] | 12 | 324 | 12 | 324 | 0 | 0 | 0 | 0
2016-03-29 | 3 |  |  |  |  | 3 | 2 | [35 empty] | 38 | 1026 | 18 | 486 | 0 | 0 | 0 | 0
2016-03-30 | [42 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2016-03-31 | 3 | [41 empty] | 0 | 0 | 18 | 486 | 0 | 0 | 0 | 0
TOTAL TRUCK TRIP | 43 | 0 | 0 | 0 | 0 | 23 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | TOTAL | 0
| 43 |  |  |  |  | 27 |  |  |  |  | 0 | [5 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [5 empty] | 0 | [9 empty] | FACTOR | 0.5
GRAND TOTAL ( TRIP ) | 70 | [20 empty] | 0 |  |  | TRIP
TOTAL VOLUME | 258 | 0 | 0 | 0 | 0 | 138 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
( CU. YD ) | 258 |  |  |  |  | 178 |  |  |  |  | 0 | [5 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0 |  |  |  |  | 0 | [5 empty] | 0
Grand Volume | 436 | ( Transportation Section ) | [19 empty] | 0 |  |  | CU. YDS
( cu yd) | 436 | ( Transportation Section + Contractor )

## CHEM_
| Bowery Bay Sodium Hypochlorite Balance Sheet | [6 empty] | Bowery Bay Dewatering Facility Polymer Balance Sheet | [8 empty] | Bowery Bay Dewatering Facility Ferric Chloride Balance Sheet | [7 empty] | Hypo Froth Control Building |  |  |  | Sodium Hydroxide (NaOH) |  |  |  |  | Bowery Bay Polymer For Froth control Balance Sheet
|  | 2016-03-01 | 2016 | [5 empty] | 2016-03-01 | 2016 | [7 empty] | 2016-03-01 | 2016 | [6 empty] | 2016-03-01 | 2016 | [7 empty] | 2016-03-01 | 2016
D | Storage | Truck Deliveries (gals) |  |  |  |  | D | Storage | Storage | Polymer Deliveries | [5 empty] | D | Storage | Truck Deliveries | [5 empty] | D | Storage | Truck Deliveries (gals) |  | Total | Storage | Truck Deliveries (gals) |  | Total | D | Storage | Truck Deliveries
A | Tanks |  |  |  | Disinfection |  | A | Tank #1 | Tank #2 | No. 1 |  |  |  | Total | Consumed | A | Tank #1 | No. 1 |  |  |  | Total | Consumed | A | Tanks |  |  | Consumed | Tanks |  |  | Consumed | A | Tank #1 | No. 1 |  |  |  | Total | Consumed
Y | 6 AM Read | No. 1 | No. 2 | Net |  |  | Y | 6 AM Read | 6 AM Read | Weight | % | Density | BofL | Vol | gal/day | Y | 6 AM Read | Weight | % | Desity | BofL | Vol | gal/day | Y | 6 AM Read | No. 1 | No. 2 |  | 6 AM Read | No. 1 | No. 2 |  | Y | 6 AM Read | Weight | % | Desity | BofL | Vol | gal/day
| (gal) | gals | gals | lbs | gal |  |  | (gal) | (gal) | (lb) | Conc | (lb/gal) | # | (gal) |  |  | (gal) | (lb) | Conc | (lb/gal) | # | (gal) |  |  | (gal) | gals | gals | gal | (gal) | gals | gals | gal |  | (gal) | (lb) | Conc | (lb/gal) | # | (gal)
1 | 12330 | 0 | 0 | 0 | 690 |  | 1 | 2406.9 | 2442.4 |  |  |  |  | 0 | 0 | 1 | 5374 |  |  |  |  | 0 | 0 | 1 | 1762 |  |  | 423 | 16900 |  |  | 0 | 1 | [5 empty] | 0
2 | 11640 | 0 | 0 | 0 | 1650 |  | 2 | 2406.9 | 2442.4 |  |  |  |  | 0 | 0 | 2 | 5374 |  |  |  |  | 0 | 0 | 2 | 1339 | 4653 | 5006 | 0 | 16900 |  |  | 0 | 2 | [5 empty] | 0
3 | 9990 | 0 | 0 | 0 | 1070 |  | 3 | 2406.9 | 2442.4 |  |  |  |  | 0 | 0 | 3 | 5374 |  |  |  |  | 0 | 0 | 3 | 10998 |  |  | 0 | 16900 |  |  | 0 | 3 | [5 empty] | 0
4 | 8920 | 0 | 0 | 0 | 830 |  | 4 | 2406.9 | 2442.4 |  |  |  |  | 0 | 0 | 4 | 5374 |  |  |  |  | 0 | 0 | 4 | 10998 |  |  | 1198.5 | 16900 |  |  | 0 | 4 | [5 empty] | 0
5 | 8090 | 4920 | 0 | 0 | 1020 |  | 5 | 2406.9 | 2442.4 |  |  |  |  | 0 | 0 | 5 | 5374 |  |  |  |  | 0 | 0 | 5 | 9799.5 |  |  | 2397 | 16900 |  |  | 0 | 5 | [5 empty] | 0
6 | 11990 | 0 | 0 | 0 | 880 |  | 6 | 2406.9 | 2442.4 |  |  |  |  | 0 | 0 | 6 | 5374 |  |  |  |  | 0 | 0 | 6 | 7402.5 |  |  | 1621.5 | 16900 |  |  | 0 | 6 | [5 empty] | 0
7 | 11110 | 0 | 0 | 0 | 1170 |  | 7 | 2406.9 | 2442.4 |  |  |  |  | 0 | 0 | 7 | 5374 |  |  |  |  | 0 | 0 | 7 | 5781 |  |  | 2608.5 | 16900 |  |  | 0 | 7 | [5 empty] | 0
8 | 9940 | 0 | 0 | 0 | 970 |  | 8 | 2406.9 | 2442.4 |  |  |  |  | 0 | 0 | 8 | 5374 |  |  |  |  | 0 | 0 | 8 | 3172.5 | 4441.5 |  | 415 | 16900 |  |  | 0 | 8 | [5 empty] | 0
9 | 8970 | 4680 | 0 | 0 | 690 |  | 9 | 2406.9 | 2442.4 |  |  |  |  | 0 | 0 | 9 | 5374 |  |  |  |  | 0 | 0 | 9 | 7199 | 4786 |  | 2679 | 16900 |  |  | 0 | 9 | [5 empty] | 0
10 | 12960 | 0 | 0 | 0 | 930 |  | 10 | 2406.9 | 2442.4 |  |  |  |  | 0 | 0 | 10 | 5374 |  |  |  |  | 0 | 0 | 10 | 9306 |  |  | 1904 | 16900 |  |  | 0 | 10 | [5 empty] | 0
11 | 12030 | 0 | 0 | 0 | 970 |  | 11 | 2406.9 | 2442.4 |  |  |  |  | 0 | 0 | 11 | 5374 |  |  |  |  | 0 | 0 | 11 | 7402 |  |  | 2820 | 16900 |  |  | 0 | 11 | [5 empty] | 0
12 | 11060 | 0 | 0 | 0 | 880 |  | 12 | 2406.9 | 2442.4 |  | 41 | 8.67 |  | 0 | 0 | 12 | 5374 |  |  |  |  | 0 | 0 | 12 | 4582 |  |  | 1974 | 16900 |  |  | 0 | 12 | [5 empty] | 0
13 | 10180 | 0 | 0 | 0 | 870 |  | 13 | 2406.9 | 2442.4 |  |  |  |  | 0 | 0 | 13 | 5374 |  |  |  |  | 0 | 0 | 13 | 2608 | 4512.5 |  | 0 | 16900 |  |  | 0 | 13 | [5 empty] | 0
14 | 9310 | 0 | 0 | 0 | 1950 |  | 14 | 2406.9 | 2442.4 |  |  |  |  | 0 | 0 | 14 | 5374 |  |  |  |  | 0 | 0 | 14 | 7120.5 |  |  | 2472.5 | 16900 |  |  | 0 | 14 | [5 empty] | 0
15 | 7360 | 4970 | 0 | 0 | 1070 |  | 15 | 2406.9 | 2442.4 |  |  |  |  | 0 | 0 | 15 | 5374 |  |  |  |  | 0 | 0 | 15 | 4648 |  |  | 2533 | 16900 |  |  | 0 | 15 | [5 empty] | 0
16 | 11260 | 0 | 0 | 0 | 1120 |  | 16 | 2406.9 | 2442.4 |  |  |  |  | 0 | 0 | 16 | 5374 |  |  |  |  | 0 | 0 | 16 | 2115 | 4723 |  | 563.5 | 16900 |  |  | 0 | 16 | [5 empty] | 0
17 | 10140 | 0 | 0 | 0 | 1380 |  | 17 | 2406.9 | 2442.4 |  |  |  |  | 0 | 0 | 17 | 5374 |  |  |  |  | 0 | 0 | 17 | 6274.5 |  |  | 2185.5 | 16900 |  |  | 0 | 17 | [5 empty] | 0
18 | 8760 | 0 | 0 | 0 | 770 |  | 18 | 2406.9 | 2442.4 |  |  |  |  | 0 | 0 | 18 | 5374 |  |  |  |  | 0 | 0 | 18 | 4089 |  |  | 2185.5 | 16900 |  |  | 0 | 18 | [5 empty] | 0
19 | 7990 | 4870 | 0 | 0 | 1170 |  | 19 | 2406.9 | 2442.4 |  |  |  |  | 0 | 0 | 19 | 5374 |  |  |  |  | 0 | 0 | 19 | 1903.5 | 4582.5 |  | 846 | 16900 |  |  | 0 | 19 | [5 empty] | 0
20 | 11690 | 0 | 0 | 0 | 1020 |  | 20 | 2406.9 | 2442.4 |  |  |  |  | 0 | 0 | 20 | 5374 |  |  |  |  | 0 | 0 | 20 | 5640 | 4723.5 |  | 2256 | 16900 |  |  | 0 | 20 | [5 empty] | 0
21 | 10670 | 0 | 0 | 0 | 1070 |  | 21 | 2406.9 | 2442.4 |  |  |  |  | 0 | 0 | 21 | 5374 |  |  |  |  | 0 | 0 | 21 | 8107.5 |  |  | 2890.5 | 16900 |  |  | 0 | 21 | [5 empty] | 0
22 | 9600 | 3560 | 0 | 0 | 780 |  | 22 | 2406.9 | 2442.4 |  |  |  |  | 0 | 0 | 22 | 5374 |  |  |  |  | 0 | 0 | 22 | 5217 |  |  | 1692 | 16900 |  |  | 0 | 22 | [5 empty] | 0
23 | 12380 | 0 | 0 | 0 | 1660 |  | 23 | 2406.9 | 2442.4 |  |  |  |  | 0 | 0 | 23 | 5374 |  |  |  |  | 0 | 0 | 23 | 3525 |  |  | 1974 | 16900 |  |  | 0 | 23 | [5 empty] | 2500
24 | 10720 | 0 | 0 | 0 | 1220 |  | 24 | 2406.9 | 2442.4 |  |  |  |  | 0 | 0 | 24 | 5374 |  |  |  |  | 0 | 0 | 24 | 1551 | 9588 |  | 705 | 16900 |  |  | 0 | 24 | 2500 |  |  |  |  | 0 | 100
25 | 9500 | 0 | 0 | 0 | 1270 |  | 25 | 2406.9 | 2442.4 |  |  |  |  | 0 | 0 | 25 | 5374 |  |  |  |  | 0 | 0 | 25 | 10434 |  |  | 2467.5 | 16900 |  |  | 0 | 25 | 2400 |  |  |  |  | 0 | 140
26 | 8230 | 0 | 0 | 0 | 1120 |  | 26 | 2406.9 | 2442.4 |  |  |  |  | 0 | 0 | 26 | 5374 |  |  |  |  | 0 | 0 | 26 | 7966.5 |  |  | 2608.5 | 16900 |  |  | 0 | 26 | 2260 |  |  |  |  | 0 | 140
27 | 7110 | 0 | 0 | 0 | 1220 |  | 27 | 2406.9 | 2442.4 |  |  |  |  | 0 | 0 | 27 | 5374 |  |  |  |  | 0 | 0 | 27 | 5358 |  |  | 1974 | 16900 |  |  | 0 | 27 | 2120 |  |  |  |  | 0 | 140
28 | 5890 | 5020 | 0 | 0 | 2330 |  | 28 | 2406.9 | 2442.4 |  |  |  |  | 0 | 0 | 28 | 5374 |  |  |  |  | 0 | 0 | 28 | 3384 |  |  | 1692 | 16900 |  |  | 0 | 28 | 1980 |  |  |  |  | 0 | 140
29 | 8580 | 0 | 0 | 0 | 1080 |  | 29 | 2406.9 | 2442.4 |  |  |  |  | 0 | 0 | 29 | 5374 |  |  |  |  | 0 | 0 | 29 | 1692 |  |  | 0 | 16900 |  |  | 0 | 29 | 1840 |  |  |  |  | 0 | 140
30 | 7500 | 0 | 0 | 0 | 1610 |  | 30 | 2406.9 | 2442.4 |  |  |  |  | 0 | 0 | 30 | 5374 |  |  |  |  | 0 | 0 | 30 | 1692 | 4794 |  | 423 | 16900 |  |  | 0 | 30 | 1700 |  |  |  |  | 0 | 140
31 | 5890 | 5020 | 0 | 0 | 1260 |  | 31 | 2406.9 | 2442.4 |  |  |  |  | 0 | 0 | 31 | 5374 |  |  |  |  | 0 | 0 | 31 | 6063 |  |  | 1833 | 16900 |  |  | 0 | 31 | 1560 |  |  |  |  | 0 | 80
1 | 9650 | [5 empty] | 1 | 2406.9 | 2442.4 | 0 | 41 | 8.67 |  |  |  | 1 | 5374 | [6 empty] | 1 | 4230 |  |  |  | 16900 |  |  |  | 1 | 1480
|  |  |  | TOTAL= | 35720 |  | Last day | 2406.9 | 2442.4 | Total | Average | Average | TOTAL= |  | 0 | [6 empty] | Total = | 0 |  |  |  | total | 49342 |  |  |  | 0 | [6 empty] | Total = | 1020
|  |  |  | AVG. = | 1152 | [7 empty] | AVG. = |  | 0 | [11 empty] | average | 1592 |  |  |  | 0
[24 empty] | * The level senor meter is malfunction, the hypo usage is approximate number. | [8 empty] | * Polymer addition system was set up on March 24th, the start dosage rates are 5mg/h for South battery and 3.33 mg/L for North Battery
|  | Summary | [30 empty] | Lowered polymer dosage rates to 2.5mg/h for SB and 1.67 mg/h for NB ON March 31st.
|  | Hypo |  |  | Polymer |  |  |  | Ferric Chloride |  | Caustic | [21 empty] | * Pipe in the suction end is bended, the pumps didn't pump as set flowrate
|  | Disinfection | Dewatering | Froth Control | Dewatering | Struvite | Thickening | Other | Dewatering | Other | SCT
|  | 35720 | 0 | 49342 | 0 | 0 | 0 | 1020 | 0 | 0 | 0

## FER
Bowery Bay WPCP Monthly Report
2016-03-06
| Week of |  | Dry Flow | Total Flow | Air | Blower Energy | SDI |  | Sludge prod | Chlorides (mg/L) |  | Thickened sludge |  | Digested Sludge |  | Volatile Dest. | Aerator Effluent (mg/L) |  | Average Aerator (mg/L) |  | Digester gas venting & Location | Aer Eff DO (mg/L) | DewateringCake | Polymer Dosage
| (Sun - Sat) |  | (mgd) | (mgd) | (MCF/d) | kwh/d | South | North | (1000 cuft/d) | High Level | Low Level | %sol | %vol | %sol | %vol | % | South | North | South | North |  |  | % | #/DT
2016-02-28 | 2016-02-28 | 2016-03-05 | 87 | 91 | 95.8 | 55.9 | 1.3 | 0.8 | 61.7 | 96 | 160 | 3.6 | 80.5 | 2.2 | 68.1 | 48% | 2960 | 3040 | 4020 | 3920 | Yes | 4.2 | #DIV/0! | 0
| 2016-03-06 | 2016-03-12 | 88 | 88 | 98.8 | 56.1 | 1.2 | 0.7 | 60.8 | 137 | 340 | 3.6 | 83.5 | 1.9 | 68 | 57% | 2800 | 2900 | 4140 | 4720 | Yes | 4 | #DIV/0! | #DIV/0!
| 2016-03-13 | 2016-03-19 | 88 | 95 | 97.4 | 54.9 | 1.5 | 0.9 | 61.1 | 1520 | 1190 | 3.5 | 80.6 | 1.7 | 67.1 | 60% | 2740 | 2800 | 3740 | 3840 | Yes | 4 | #DIV/0! | #DIV/0!
| 2016-03-20 | 2016-03-26 | 89 | 90 | 95.7 | 55.4 | 1.2 | 0.9 | 66.6 | 111 | 220 | 2.9 | 82.9 | 1.9 | 68.6 | 46% | 3200 | 3320 | 4580 | 4660 | Yes | 3.5 | #DIV/0! | #DIV/0!
| Monthly Avg |  | 87 | 91 | 96.6 | 55.6 | 1.2 | 0.8 | 65.7258 | 390 | 430 | 3.4 | 82.1 | 1.9 | 69.1 | 53% | 3000 | 3000 | 4200 | 4200 |  | 3.9 | #N/A | #N/A
| Week of |  | Total Suspended Solids (mg/L) |  |  | 5-day CBOD (mg/L) |  |  | Total Nitrogen (mg/L) |  |  | Total Nitrogen (lb/d) |  | Hypo for Disinfection | Cl2 Residual | Sludge Age (day) |  | SRT (day) |  | 7-day geometric FC average | Caustic | Glycerin | Ferric Chloride | Hypo for other uses
| (Sun - Sat) |  | Influent | Final Eff | % Rem | Influent | Final Eff | % Rem | Influent | Effluent | % Rem | Influent | Effluent | (gpd) | (mg/L) | South | North | South | North | (#/100ml) | gals/day | gals/day | gals/day | gals/day
| 2016-02-28 | 2016-03-05 | 130 | 20 | 85% | 151 | 8 | 95% | 37.2 | 16.5 | 56% | 28231.5 | 12605.8 | 917 | 0.47 | 11.8 | 11.9 | 5.1 | 9.9 | 91 | 0 | 0 | 0 | 1200
| 2016-03-06 | 2016-03-12 | 155 | 9 | 94% | 143 | 6 | 96% | 38.8 | 14.5 | 63% | 28391 | 10580.1 | 927 | 0.46 | 12.8 | 12.7 | 5.4 | 10.1 | 90 | 0 | 0 | 0 | 2000
| 2016-03-13 | 2016-03-19 | 165 | 10 | 94% | 135 | 5 | 96% | 37 | 13.4 | 64% | 28746.8 | 10686 | 1190 | 0.46 | 11.1 | 10.8 | 4.7 | 8.1 | 78 | 0 | 0 | 0 | 1540
| 2016-03-20 | 2016-03-26 | 145 | 9 | 94% | 157 | 5 | 97% | 39.5 | 12.6 | 68% | 29729 | 9474.4 | 1163 | 0.45 | 13.7 | 13 | 5.4 | 8.1 | 30 | 0 | 0 | 0 | 2080
| Monthly Avg |  | 149 | 12 | 92% | 144 | 6 | 96% | 37.9 | 13.6 | 64% | 28500 | 10400 | 1152 | 0.46 | 12.5 | 11.7 | 5.1 | 8.4 | 67 | 0 | 0 | 0 | 1592
Some of the monthly average data were from DMR. cBOD data were 5days behind
Notes/Comments:
1. Started flare digester gas for digester #6 on 3/27/2014 , started flare digester gas for digester #3 on 5/23/2014 and started flare digester gas for digester #7 on 2/28/2015. All Digester gas are flared after 7/15/2015.
2. Process air cfm, blower KW, SWAS rate North & South, Aerator effluent DO readings, CCT effluent flows (used for reporting) were taken from DCS. Started from Feb 2014, RAS rate was taken from DCS.
3. Only SWAS pumps were in service for wasting started on 1/7/2014.
4. Primary Tank #12 OOS for maintance on 9/9/2014, to replace a new Screw collector in the tank and returned back to service on 10/22/2015.
5. Force Main "A" Leakage, plant switched to emergency mode on 6/5/2015.
6. Only Operating two blowers from 11/9/2015
7. Target TRC set to 0.4mg/L on 11/9/2015.
8. Digester No.7 is venting digas from 10/7/2015.
9. Started running Caustic system on 11/23/2015. Caustic is only feeding to SCT at approximate rate of 350 gal/day. Shut off the caustic system on 1/4/2016 due to dewatering shut down.
10. Dewatering shut down on 1/4/2016 for belt contract work.
11. Final Tank No. 4 OOS due to chain problem on 1/11/2016
12. Final Tank No. 7 OOS due to flight issue on 1/14/2016.
13. Final Tank No. 13 OOS due to flight broke on 2/11/2016
14. Primary Tank No. 6 OOS due to cross-collector issue on 2/28/2016 and returned back to service on 3/5/2016. PST No. 6 OOS on 3/18/2016 due to cross-collector issue and that work is ongoing.
15. Contact tank No. 3 OOS for PM on 3/9/2016 and returned back to service on 3/11/2016
16. Contact Tank No. 2 OOS for PM on 3/21/2016 and returned back to service on 3/23.
17. Contact Tank No. 1 OOS for PM on 3/23/2016 and returned back to service on 3/25/2016
18. PST no. 8 OOS due to cross-collector chain issue on 3/9/2016 and returned back to service on 3/24/2016. Pst No. 8 oos on 3/28/2016 due to flight chain broken and that work is on going.
19. Plant started polymer addition to aeration tanks for froth control on 3/24/2016, the dosage rate is 2ppm/1mgd for both batteries. Plant lowered dosage rate to 1ppm/1mgd on 3/31/2016.
Formulas:
Air = IF(C7>TODAY(),"",IF([Dry Flow]="","",ROUND(1-[Total Flow]/[Dry Flow],2)))
Blower Energy = IF([Dry Flow]>TODAY(),"",+VLOOKUP(C7,AT_!$AQ83:CC113,28))
Volatile Dest. = IF(C7>TODAY(),"",ROUND((([Thickened sludge]*N7)-([Digested Sludge]*P7))/([Thickened sludge]*N7),2))
Week of = +[Week of, row above]+7

## Energy Report
MONTHLY ENERGY REPORT
BUREAU OF WASTEWATER TREATMENT
LOCATION: | Bowery Bay | [5 empty] | LOCATION #:_______________________ | [5 empty] | 2016-03-01 | 2016
[11 empty] | SLUDGE PRODUCTION: |  |  |  | 2037500 |  | CUFT
TOTAL SEWAGE FLOW: |  |  | 2828 |  | MG/MONTH | [5 empty] | SLUDGE TO DEWATERING: |  |  |  | 0 |  | CUFT
GENERATED
ELELCTRICITY | FEEDER # 1 |  | FEEDER # 2 |  | FEEDER # 3 |  | FEEDER # 4 |  |  | Total |  |  | GENERATORS |  | FUEL CELLS |  | TOTAL
KWH | [9 empty] | 4121600 |  |  | 0
KW
FUEL (GALLONS) | #1DLS |  |  | #2DLS |  |  | #2D |  |  | #2 |  |  | #4 |  |  | TOTAL
BEGIN OF MONTH
END OF MONTH
DEWAT BOILERS
PLANT BOILERS | [15 empty] | 0
EMERGENCY GEN (by dw) | [15 empty] | 4
BLACK START GEN
GENERATORS (by P&B bld) | [15 empty] | 250
PUMP ENGINES
BLOWER ENGINES
TOTAL CONSUMPTION | [15 empty] | 254
TOTAL DELIVERIES
UTILITY GAS | Plant BOILERS |  |  | ENGINES |  |  | DEWATERING |  |  | MAIN PLANT |  |  | FUEL CELLS |  |  | TOTAL
CUFTX1000 | 9704 | [5 empty] | 83 | [8 empty] | 9787
| PUMP ENG |  |  | BLOWER ENG
DIGESTER GAS | PRODUCED |  |  | BOILERS |  | ENGINES |  |  | FUEL CELLS |  | FLARED |  | VENTED |  |  | TOTAL WASTED
CUFTX1000 | 28263 | [9 empty] | 21194.7 |  | 7068.3
|  |  |  | PUMP ENG |  |  |  | BLOWER ENG |  |  | ENGINES |  |  |  |  | TOTAL USED
M. VEHICLE FUEL(GAL) | ON HAND START OF MONTH |  |  |  |  | DELIVERED |  |  | USED |  |  | ON HAND END OF MONTH
DIESEL | 2324 |  |  |  |  | 0 |  |  | 259 |  |  | 2065
GASOLINE | 2265 |  |  |  |  | 0 |  |  | 534 |  |  | 1731
WATER CONSUMPTION |  | CONSUMPTION THIS MONTH | [6 empty] | PREVIOUS MONTH CONSUMPTION
CUFT |  | 2734600
STEAM |  | HEATING |  |  |  | PROCESS |  |  | TOTAL
MILLION LBS
Comments: | Digester gas produced is a calculated value. One flare was in service since 1/30/2013 burning gas produced from Digester 6 & 7 (total of 4 primary digesters are in service during the month). Thre rest of digester gas produced was vented out. Started venting digester gas 100% on 11/14/13.
PLANT SUPERINTENDENT | [8 empty] | ENERGY MANAGER
| storage tanks reading | [7 empty] | temporary generators |  |  |  |  | natural gas x1000 cuft | natural gas x1000 cuft |  | Water Consumption Meter
| date | emg gen #9 | diesel #12 | gasoline #11 |  |  | permanent boilers |  | #1 - 18 | #2 - 19
|  | dw | toolroom |  |  |  | #14, 15, 16 |  | by P&B bld |  |  |  |  | P&B building | DW build |  | Berrian 1 | Berrian 2 | Steinway
| 2016-03-01 | 3719 | 2324 | 2265 |  |  | 17548 |  | 750 | 750 |  |  |  | 168665 | 2972 |  | Removed | 69846200 | 83848900
| 2016-04-01 | 3723 | 2065 | 1731 |  |  | 17548 |  | 750 | 500 |  |  |  | 178369 | 3055 |  |  | 71965000 | 84464700
| deliveries | 9 | 12 | 11 |  |  | 14 | 15 | 16 | 18 | 19

## Sheet1 (hidden)
Flow MGD | 91 |  |  |  | 65.4929 |  | 59.6571 |  |  | 111.4636 |  |  |  | 59.6571 |  |  |  |  | 91 |  | 6
TSS lb/d | 114600 |  |  |  | 113329.4223 |  | 37813.0818 |  |  | 2788819.07 | [8 empty] | 9800 | 91.45%
BOD lb/d | 107600 |  |  |  | 77439.9271 |  | 43286.0279 |  |  | - | [8 empty] | 4500 | 95.82%
| Influent |  |  |  | To South
[6 empty] | 9 |  |  | 6 |  | 51.8065 | 9
[11 empty] | 2938047.4839 | RAS
[5 empty] | 36.3849 |  | 32.4944 |  |  |  | - |  | 1.7129 |  | 32.4944
[5 empty] | 1270.5777 |  | 23035.309 |  |  | 137.817 |  | WAS | 97139.1552
[5 empty] | 30160.0729 |  | 23306.3127 |  |  | 3448181.8752 |  |  | -
[5 empty] | To North |  |  |  |  | -
[6 empty] | 6 |  |  | 3 |  |  | 5
[11 empty] | 105.3226 | RAS
[11 empty] | 4743307.7419 |  | 0.57877
|  |  |  | 11.3694 | [6 empty] | - | WAS | 26065.7095
|  | 10.8778 |  | 269192.3245 | [8 empty] | - | #VALUE! |  |  |  | #VALUE!
|  | 61690.2125 |  | - | [9 empty] | #VALUE! |  |  |  | #VALUE! | TS lb/d
|  | - | [11 empty] | - |  |  |  | -
[5 empty] | 0.49163 |  |  |  | 0.49163 |  |  |  |  | Sludge Feed |  |  | Cake
| thickener overflow |  |  |  | 139187.0968 |  |  |  | #VALUE!
[5 empty] | - |  |  |  | -
|  |  |  | Thickened Sludge |  |  |  | Digested Sludge | [7 empty] | Centrate | #VALUE!
to AT 10
|  |  | TSS | TS (chloride)
|  | in | 114600 | 303576
|  | out | 148987.0968 | 452563.0968
|  | in - out | -34387.0968 | -148987.0968
|  | % | -30.01% | -49.08%
typ - -10%
| inf | PST | AT | FST | CCT | Effl
in | 114600 | 114600 | 3083748.6489 | 6237000.9451 |  | 9800
out eff |  | 23035.309 | 2295958.487 | 9800 |  | 9800
out - sludge |  |  |  | 3145519.3548
out total | 0 | 23035.309 | 2295958.487 | 3155319.3548 | 0 | 9800
in - out | 114600 | 91564.691 | 787790.162 | 3081681.5903 | 0 | 0
South
PST
North
PST
South
AT
South
FST
North
AT
North
FST
CCT
Division Structure
Thickeners
Digesters
Dewatering
Storage